## INDEX
Uttar Gujarat Vij Company Limited, Mehsana
Performas for FY 2023-24
Performa No. | Particulars | Remarks/Report
SoP 001 | Fatal & Non Fatal Accident Report | Qtrly FY 2023-24
SoP 003 | Register for compiling the complaints classification wise | Qtrly FY 2023-24
SoP 004 | Actions or steps carried out by UGVCL towards public awareness in the year | Qtrly FY 2023-24
SoP 005 | Action taken report by the Redressal Committee | Qtrly FY 2023-24
SoP 006 | Failure of Distribution Transformer. | Qtrly FY 2023-24
SoP 011 A | System Average Interruption Frequency Index (SAIFI) | Qtrly FY 2023-24
SoP 011 B | System Average Interruption Duration Index (SAIDI) | Qtrly FY 2023-24
SoP 011 C | Momentary Average Interruption Frequency Index (MAIFI) | Qtrly FY 2023-24
SoP 013 | Meter Faults | Qtrly FY 2023-24
SoP 016 | Compensation Details | Qtrly FY 2023-24

## SoP001
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr.-23 to June-23)
YEAR :- 2023-24
Performa - SOP 001 : Fatal and Non-fatal accident report for quarter ending
Sr. No. | Name of area | No.of accidents during the quarter |  |  |  |  | Cumulative since the first quarter of the current FY
|  | Departmental |  | Out side
|  | FH | NFH | FH | FA | NFH | FH | FA | NFH
1 | Sabarmati | 0 | 4 | 10 | 11 | 2 | 10 | 11 | 6
2 | Mehsana | 0 | 0 | 7 | 5 | 1 | 7 | 5 | 1
3 | Palanpur | 2 | 2 | 5 | 14 | 3 | 7 | 14 | 5
4 | Himatnagar | 0 | 1 | 9 | 10 | 3 | 9 | 10 | 4
| TOTAL | 2 | 7 | 31 | 40 | 9 | 33 | 40 | 16

## SoP 003
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
Performa SoP 003 B:
APPENDIX - B
REGISTER FOR COMPILING THE COMPLAINTS CLASSIFICATION WISE
Classification | Pending complaint of previous quarter | Complaints received during the quarter | Total complaints | No.of complaints redressed during the month |  |  |  |  | Balance complaints to be redressed (4) - (9) | Classification of complaint
|  |  |  | In stipulated time |  | Beyond stipulated time |  | Total (5) to (8)
|  |  |  | Within 50% of stipulated time | Within stipulated time | Upto double the stipulated time | More than double the stipulated time
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
A(i) | 0 | 32548 | 32548 | 20914 | 11634 | 0 | 0 | 32548 | 0 | Loose conn. from pole
A(ii) | 0 | 23890 | 23890 | 19333 | 4557 | 0 | 0 | 23890 | 0 | Int.due to line breakdown
A(iii) | 0 | 5846 | 5846 | 1932 | 3914 | 0 | 0 | 5846 | 0 | Interruption due to failure of transformer
B(i) | 0 | 1828 | 1828 | 1075 | 753 | 0 | 0 | 1828 | 0 | Ordinary case, which requires no augmentation
B(ii) | 0 | 1561 | 1561 | 588 | 973 | 0 | 0 | 1561 | 0 | Where augmentation is required
C(i) | 0 | 7130 | 7130 | 4890 | 2224 | 16 | 0 | 7130 | 0 | Stopped/Defective Meters
C(ii) | 0 | 3408 | 3408 | 2305 | 1103 | 0 | 0 | 3408 | 0 | Billing on average basis for more than two bills
D(i) | 0 | 4059 | 4059 | 2036 | 2023 | 0 | 0 | 4059 | 0 | Loose Wires
D(ii) | 0 | 477 | 477 | 218 | 259 | 0 | 0 | 477 | 0 | Inadequate ground clearance
E(i) | 0 | 1696 | 1696 | 895 | 801 | 0 | 0 | 1696 | 0 | For current bills where no additional information is required
E(ii) | 0 | 1550 | 1550 | 708 | 842 | 0 | 0 | 1550 | 0 | Where additional information relating to correctness of reading etc. is required
F(i) | 0 | 1189 | 1189 | 649 | 540 | 0 | 0 | 1189 | 0 | Where extension of mains is not required
F(ii) | 0 | 423 | 423 | 282 | 141 | 0 | 0 | 423 | 0 | Where extension of mains is required
F(iii) | 0 | 2399 | 2399 | 1483 | 916 | 0 | 0 | 2399 | 0 | Modification in connected load
F(iv) | 0 | 1922 | 1922 | 1121 | 801 | 0 | 0 | 1922 | 0 | Name change/reconnection
G | 0 | 597 | 598 | 395 | 203 | 0 | 0 | 598 | 0 | Refund of amount due in regard to temporary connection
H | 0 | 7596 | 7596 | 4954 | 2642 | 0 | 0 | 7596 | 0 | Others
Total | 0 | 98119 | 98120 | 63778 | 34326 | 16 | 0 | 98120 | 0

## SoP 004
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
Performa SoP 004
Sr. No. | Actions or steps carried out by UGVCL towards public awareness in the quarter | Likely number of consumers influenced | Details about media
1 | Display board of SOP at circle, Division & S/Dn | 105371 | Notice Board
2 | Display board of Name of information officers under RTI Act 2005 at Circle,Division,Sub- division offices. | 109002 | Notice Board
3 | Consumer care centers at various places | 161241 | Verbal & Notice Board at CCC
4 | Advertisement through Daily News papers | 100713 | Daily News papers
5 | Pamphlets distributed among public | 143023 | Pamphlets
6 | Advertisement through slide in TV / Banners | 104459 | T V Channels
7 | On Web site of Uttar Gujarat Vij Company Limited | 127265 | Internet
8 | Through Regular Energy Bills | 2484321 | Energy Bill
9 | Others | 1120 | CD

## SoP 005
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
YEAR :- 2023-24
Performa SoP 005 B: Action taken report by the Redressal Committee
Sr. No. | Month | Date and time meeting conducted | No. of complaints registered at the meeting | No. of complaints pending at the end of the meeting | Nos of cases Disposed | Location of Hearing
1 | Apr.23 | 11.04.2023 | 1 | 0 | 1 | Corporate Office, Mehsana
|  | 12.04.2023 | 2 | 2 | 0 | Circle office Sabarmati
|  | 21.04.2023 | 2 | 0 | 2 | Circle office Sabarmati
|  | 28.04.2023 | 1 | 0 | 1 | Corporate Office, Mehsana
2 | May.23 | 11.05.2023 | 3 | 1 | 2 | Circle office Sabarmati
|  | 20.05.2023 | 2 | 0 | 2 | Corporate Office, Mehsana
|  | 26.05.2023 | 5 | 5 | 0 | Circle office Sabarmati
3 | June.23 | 09.06.2023 | 5 | 1 | 4 | Circle office Sabarmati
|  | 30.06.2023 | 3 | 2 | 1 | Circle office Sabarmati

## SoP 006
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr.- 23 to June- 23)
Performa SoP 006 : Failure of Distribution Transformer.
Sr. No. | Class | No. of existing Distribution transformer at the start of the quarter | No.of Distribution transformers added during the quarter | Total number of Distribution transformers | Total number of Distribution transformer failed during the quarter | % failure rate of Distribution transformer
|  | A | B | C=A+B | D | H= (D) * 100/C
1 | 11KV | 395509 | -667 | 394842 | 7542 | 1.9101
Total |  | 395509 | -667 | 394842 | 7542 | 1.9101

## SOP011-(AG)
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
YEAR :- 2023-24
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for AG. Dominant Category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2023-04-01 | 432735 | 638506 | 1398582 | 2.1904
2 | 2023-05-01 | 531711 | 639792 | 2250843 | 3.5181
3 | 2023-06-01 | 574334 | 641514 | 3185335 | 4.9653
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for AG. Dominant Category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 1901-03-20 17:13 | 432735 |  | 638506 | 2164-05-30 01:20 | 0.15125
2 | 2023-05-01 | 1902-09-29 04:47 | 531711 |  | 639792 | 204772.5528 | 0.32006
3 | 2023-06-01 | 1904-04-21 20:06 | 574334 |  | 641514 | 295951.2014 | 0.46133
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for AG. Dominant Category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 12588 | 561473 |  | 638506 | 3137990 | 4.9146
2 | 2023-05-01 | 14662 | 579981 |  | 639792 | 3433977 | 5.3673
3 | 2023-06-01 | 18083 | 605047 |  | 641514 | 4069236 | 6.3432

## SOP011-(JGY)
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
YEAR :- 2023-24
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2023-04-01 | 1491705 | 2152188 | 3856234 | 1.7918
2 | 2023-05-01 | 1951667 | 2154975 | 8567233 | 3.9756
3 | 2023-06-01 | 1997685 | 2141140 | 12857004 | 6.0047
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 1900-04-09 13:09 | 1491705 |  | 2152188 | 2437-11-06 04:45 | 0.091278
2 | 2023-05-01 | 1900-08-10 11:55 | 1951667 |  | 2154975 | 440710.7271 | 0.20451
3 | 2023-06-01 | 1900-12-28 08:06 | 1997685 |  | 2141140 | 682435.8493 | 0.31873
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 4788 | 2028061 |  | 2152188 | 10553657 | 4.9037
2 | 2023-05-01 | 6567 | 2070963 |  | 2154975 | 14917352 | 6.9223
3 | 2023-06-01 | 8102 | 2095017 |  | 2141140 | 18097672 | 8.4524

## SOP011-(OTHER THAN AG-JGY)
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
YEAR :- 2023-24
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for Other than AG & JGY category
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2023-04-01 | 774665 | 1276847 | 1790235 | 1.4021
2 | 2023-05-01 | 990324 | 1279534 | 3861625 | 3.018
3 | 2023-06-01 | 1004386 | 1296658 | 5301319 | 4.0884
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for Other than AG & JGY category
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 1900-03-01 11:33 | 774665 |  | 1276847 | 2057-06-24 13:30 | 1:05
2 | 2023-05-01 | 1900-05-12 18:34 | 990324 |  | 1279534 | 2258-06-05 21:03 | 2:27
3 | 2023-06-01 | 1900-06-05 06:20 | 1004386 |  | 1296658 | 2404-01-04 19:54 | 3:24
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for Other than AG & JGY category
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 1692 | 955365 |  | 1276847 | 3176297 | 2.4876
2 | 2023-05-01 | 2432 | 1049944 |  | 1279534 | 4215109 | 3.2943
3 | 2023-06-01 | 2855 | 1126702 |  | 1296658 | 5049909 | 3.8946

## SOP011-(OVERALL)
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
YEAR :- 2023-24
SoP 011 - A : System Average Interrruption Frequency Index (SAIFI) for UGVCL as a whole
Sr. No | Month | Ni - Number of Customers for each sustained interruptions (in numbers) | NT - Total No of customers served (in Numbers) | CI=∑ Ni | SAIFI = ∑ Ni/Nt (Monthly SAIFI)
1 | 2 | 3 | 4 | 5 | 6=5/4
1 | 2023-04-01 | 2699105 | 4067541 | 7045051 | 1.732
2 | 2023-05-01 | 3473702 | 4074301 | 14679701 | 3.603
3 | 2023-06-01 | 3576405 | 4079312 | 21343658 | 5.2322
SoP 011 - B : System Average Interrruption Duration Index (SAIDI) for UGVCL as a whole
Sr. No | Month | Ri = Restoration Time for each sustained interruption event (in hours) | Ni - Number of interrupted Customers for each sustained interruption event (in numbers) | Ri* Ni - Total customer interrution Duration | NT - Total No of customers served (in Numbers) | Customer Intt. Duration CMI = ΣRi*Ni | SAIDI = ΣRi*Ni/Nt (Monthly SAIDI)
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 1901-08-29 17:55 | 2699105 |  | 4067541 | 350543.816 | 2:04
2 | 2023-05-01 | 1903-09-21 11:16 | 3473702 |  | 4074301 | 776398.1569 | 4:34
3 | 2023-06-01 | 1905-09-24 10:32 | 3576405 |  | 4079312 | 1162474.8799 | 6:50
SoP 011 - C : Momentary Average Interruption Frequency Index (MAIFI) for UGVCL as a whole
Sr. No | Month | IMi = Number of Momentary interruptions for the month (in numbers) | Nmi = Total no of customers for each momentary interruptions (in numbers) | Imi =Nmi Number of customer Momentary interruptions (in numbers) | Nt - Total no of customers served (in numbers) | Customer Intt. ΣImi*Nmi | MAIFI=ΣImi*Nmi/Nt
1 | 2 | 3 | 4 | 5 = 3 * 4 | 6 | 7 | 8=7/6
1 | 2023-04-01 | 19068 | 3544899 |  | 4067541 | 16867944 | 4.147
2 | 2023-05-01 | 23661 | 3700888 |  | 4074301 | 22566438 | 5.5387
3 | 2023-06-01 | 29040 | 3826766 |  | 4079312 | 27216817 | 6.6719

## SoP013
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
Performa SoP 013 : Meter faults
Consumer Category | No. of faulty meters at the start of the quarter | No. of faulty meters added during the quarter | Total No. of defective / faulty meter | No. of faulty Meters repaired and replaced | No. of faulty meters pending at the end of the quarter
| 1 | 2 | 3=2+1 | 4 | 5=3-4
Single Phase | 830 | 20535 | 21365 | 19497 | 1868
Three Phase | 441 | 7986 | 8427 | 7234 | 1193
Total | 1271 | 28521 | 29792 | 26731 | 3061

## SoP016
Uttar Gujarat Vij Company Limited
QUARTER :- 1st (Apr. - 23 to June - 23)
Performa SoP 016 : Compensation details
COMPENSATION DETAILS
Sr. No. | Event | Compensation | No. of cases where compensation was given (in numbers) | Amt.of compensation paid (in Rs.)
1 | Duty to provide supply | Rs.50 per day of delay from the limit specified in the performance regulations | …NIL… | …NIL…
a) New connection
b) Additional load
c) Temporary supply
d) Shifting service connection
e) Transfer of service connection
f) Change in tariff category of consumer
2 | Complaints in billing | Rs.50 for non reply within the period prescribed in Regulations
3 | Replacement of meters | LT Rs.25 per day of delay maximum Rs.2,500 and HT Rs. 250 per day of delay maximum of Rs. 5,000/-
4 | Interruption of supply | LT Rs.25 for every 6 hrs. of delay maximum of Rs.500 and HT Rs. 50 for every 6 hrs. delay maximum Rs. 1000
5 | Voltage fluctuations and complaints | Rs.50 for failure to visit or convey findings within the stipulated period
6 | Responding to consumers complaints | Rs. 25 for each day of delay maximum Rs. 500
7 | Grievance Handling | Rs. 25 for failure in handling grievance.
| TOTAL :- |  | …NIL… | ……NIL…..