## Front
UGVCL
Cost Data & Labour Rates
2022-23

## Annexure-E
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM WISE COST DATA (RE/CITY) FOR FY 2022-23
ANNEXURE-E
SR NO. | ITEM CODE | ITEM NO | PARTICULARS | UNIT | RATE OF 2014-15 | RATE OF 2015-16 | RATE OF 2019-20 | RATE (In Rs.) 22-23 | % Variation | Correct Item Code
1 | 9601000001 | ITEM 1 | TAPPING FROM EXISTING POLES FOR 11 KV LINE | NO | 6235.5375 | 5918 | 6498 | 8612 | 32.53%
2 | 9601000002 | ITEM 2 | GUARDING UNDER HT AND LT LINE (SPAN-60 MTR) | NO | 7392.228 | 7518 | 8238 | 9285 | 12.71%
3 | 9601000003 | ITEM 3 | 11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 8 MTR POLE | NO | 36033.4172 | 36744 | 38929 | 48716 | 25.14%
4 | NEW | ITEM 4 | 11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 10 MTR POLE | NO |  |  | 44681 | 57262 | 28.16% | 9601000089
5 | 9602000104 | ITEM 5 | 11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH On RSJ 9 MTR POLE | NO | 57552.3372 | 55216 | 70233 | 89741 | 27.78%
6 | 9601000004 | ITEM 6 | 11 KV DOUBLE POLE STRUCTURE WITH HG FUSE (WITHOUT AB SWITCH) On PSC 8 MTR POLE | NO | 31884.1972 | 31223 | 31950 | 39655 | 24.12%
HT LINE
7 | 9601000005 | ITEM 7 | 11KV LINE WITH 34 MM2 AAAC CONDUCTOR( SPAN 50 MTR ) ON 8 MTR PSC POLE WITH WIND PRESSURE ZONE 100 KG/M2 | KM | 205025.3684 | 210114 | 222012 | 278806 | 25.58%
8 | 9601000006 | ITEM 8 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 | KM | 243352.3973 | 251371 | 264766 | 333880 | 26.1%
9 | 9602000204 | ITEM 9 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 | KM | 316698.2737 | 321505 | 341479 | 429647 | 25.82%
10 | 9602000207 | ITEM 10 | 11KV LINE WITH DOG CONDUCTOR (SPAN-50 MTR) ON PSC POLE (10 MTR) WITH 11 KV MATERIALS | KM | 427643.704 | 441438 | 442128 | 565060 | 27.8%
11 | NEW | ITEM 11 | 11KV LINE WITH DOG CONDUCTOR (SPAN-33 MTR) ON PSC POLE (10 MTR) WITH 11 KV MATERIALS | KM |  |  | 541293 | 694480 | 28.3% | 9602000263
12 | 9602000208 | ITEM 12 | 11KV LINE WITH DOG AAAC CONDUCTOR (SPAN-33 MTR) ON RSJ POLE (9 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 887812.7126 | 875431 | 928282 | 1182624 | 27.4%
13 | 9602000209 | ITEM 13 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-50 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS | KM | 307169.3973 | 310660 | 325547 | 421428 | 29.45% | 9602000223
14 |  | ITEM 14 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS | KM |  |  | 427141 | 554694 | 29.86% | 9602000267
15 | 9601000007 | ITEM 15 | UNDER GROUND RAILWAY CROSSING (DOUBLE TRACK- BROAD GAUGE) FOR 11 KV SYSTEM | NO | 798129.8646 | 863261 | 775184 | 802658 | 3.544%
16 | 9601000008 | ITEM 16 | RIVER CROSSING (11KV) on 10 MTR PSC POLE | NO | 73308.5788 | 70862 | 72958 | 92841 | 27.25%
TRANSFORMER CENTRE ON SINGLE POLE STRUCTURE WITH OUT FENCING
17 | 9601000026 | ITEM 17 | 25 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO | 108778.9301 | 111847 | 109370 | 145014 | 32.59%
18 | 9601000044 | ITEM 18 | 16 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO | 87685.5205 | 85702 | 94791 | 129033 | 36.12%
19 | 9601000045 | ITEM 19 | 10 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO | 80416.9069 | 81375 | 80892 | 117809 | 45.64%
20 | NEW | ITEM 20 | 5 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO |  |  | 73674 | 94812 | 28.69% | 9601000090
TRANSFORMER CENTRE ON DOUBLE POLE STRUCTURE WITH OUT FENCING
21 | 9601000046 | ITEM 21 | 11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING | No | 97321.9996 | 97210 | 96596 | 138612 | 43.5% | 9601000095
22 | 9601000047 | ITEM 22 | 11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING | NO | 104245.6132 | 101077 | 110005 | 149318 | 35.74%
23 | 9601000009 | ITEM 23 | 11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING | KM | 113543.7296 | 113155 | 124985 | 165550 | 32.46%
24 | 9601000010 | ITEM 24 | 11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING | NO | 160525.6246 | 154648 | 176126 | 228742 | 29.87%
25 | 9601000011 | ITEM 25 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING | NO | 196788.929 | 194990 | 219882 | 286395 | 30.25%
26 | 9602000125 | ITEM 26 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING | NO | 227588.454 | 223534 | 252343 | 328514 | 30.19%
27 | 9602000127 | ITEM 27 | 11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING | NO | 469107.3766 | 445569 | 496701 | 739995 | 48.98%
TRANSFORMER CENTRE ON DOUBLE POLE STRUCTURE WITH FENCING
28 | 9601000046 | ITEM 28 | 11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | No | 122487.5476 | 123179 | 123285 | 167007 | 35.46% | 9601000095
29 | 9601000047 | ITEM 29 | 11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | NO | 129411.1612 | 127046 | 136538 | 177556 | 30.04% | 9601000096
30 | 9601000009 | ITEM 30 | 11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | KM | 150730.0108 | 153541 | 151518 | 193788 | 27.9% | 9601000097
31 | 9601000010 | ITEM 31 | 11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | NO | 206384.0562 | 192760 | 202658 | 256980 | 26.8% | 9601000098
32 | 9601000011 | ITEM 32 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | NO | 255752.9666 | 230022 | 246414 | 314633 | 27.68% | 9601000099
33 | 9602000125 | ITEM 33 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING | NO | 286552.4916 | 258566 | 278876 | 356752 | 27.92% | 9602000264
34 | 9602000127 | ITEM 34 | 11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING | NO | 520261.8648 | 521902 | 523233 | 768233 | 46.82% | 9602000265
35 |  | ITEM 35 | 11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON 10 MTR PSC POLE WITH FENCING | NO |  |  | 506205 | 743186 | 46.82% | 9602000266
36 | 9602000130 | ITEM 36 | 11/0.433 KV 500 KVA DIST. TRANSFORMER CENTRE ON PLINTH | NO | 1653639.136 | 1656034 | 2001321 | 2405845 | 20.21%
SPECIAL DESIGNED TRANSFORMER / PAT
37 |  | ITEM 37 | 11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER- SDT - 24 AMP | NO | New | 236437 | 243522 | 255674 | 4.99% | 9601000063
38 |  | ITEM 38 | 11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER - SDT- 30 AMP | NO | New | 253004 | 271582 | 283734 | 4.475% | 9601000064
39 |  | ITEM 39 | 11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 24.7 AMP | NO | New | 312016 | 315431 | 326873 | 3.627% | 9601000065
40 |  | ITEM 40 | 11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 54 AMP | NO | New | 432287 | 435702 | 447144 | 2.626% | 9601000066
LT LINE
41 | 9601000012 | ITEM 41 | L.T. LINE 1 PH 2 WIRE USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 158557.0844 | 163563 | 165494 | 209758 | 26.75%
42 | 9601000013 | ITEM 42 | L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR)WITH WIND PRESSURE 100 KG/M2 | KM | 184545.9682 | 191404 | 195120 | 247609 | 26.9%
43 | 96020002111 | ITEM 43 | L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN - 30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 251005.6724 | 258474 | 260755 | 332974 | 27.7%
44 | 9601000014 | ITEM 44 | L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING34 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 208276.5794 | 216994 | 222602 | 283217 | 27.23%
45 | 9602000212 | ITEM 45 | L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 307744.4635 | 317001 | 327010 | 410952 | 25.67%
46 | 9602000213 | ITEM 46 | L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 9 MTR RSJ POLES 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 790673.9519 | 764987 | 838535 | 1075708 | 28.28%
47 | 9602000143 | ITEM 47 | L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 10 MTR PSC POLES 34 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 300446.3799 | 304101 | 313632 | 406586 | 29.64%
48 | 9601000015 | ITEM 48 | L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 246529.2615 | 258147 | 265142 | 338004 | 27.48%
49 | 9602000214 | ITEM 49 | L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING PSC POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 318365.4876 | 330539 | 336847 | 430791 | 27.89%
50 | 9602000215 | ITEM 50 | L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING 9 MTR RSJ POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 829000.566 | 806243 | 881130 | 1130623 | 28.32%
51 | 9601000016 | ITEM 51 | L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (WEASEL)(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 236863.8291 | 247501 | 255144 | 324511 | 27.19%
52 | 9602000216 | ITEM 52 | L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (Span-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 307340.1626 | 318618 | 325320 | 415361 | 27.68%
53 | 9602000217 | ITEM 53 | L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING 9 MTR RSJ POLE 34 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2 | KM | 818736.8626 | 794949 | 870238 | 1116072 | 28.25%
54 | 9601000017 | ITEM 54 | L.T. LINE 3PHASE 5WIRE FOR AG PURPOSE. VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 274262.7552 | 287790 | 296751 | 378005 | 27.38%
55 | 9602000218 | ITEM 55 | L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING RSJ POLE 55 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2 | KM | 855299.4567 | 834472 | 911515 | 1169523 | 28.31%
56 | 9602000219 | ITEM 56 | L.T. LINE ADDING OF ONE WIRE IN VERTICAL FORMATION USING55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 | KM | 44558.6096 | 47574 | 50395 | 63361 | 25.73%
SERVICE CONNECTION (WITH EARTH TERMINAL)
57 | 9601000018 | ITEM 57 | SERVICE CONNECTION 3 PHASE 4 WIRE UP TO 5 HP | NO | 5926.9891 | 5850 | 6609 | 7660 | 15.9%
58 | 9601000019 | ITEM 58 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 5 HP TO 10 HP | NO | 6554.124 | 6527 | 7236 | 8421 | 16.38%
59 | 9601000020 | ITEM 59 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 10 HP TO 20 HP | NO | 7255.3861 | 7256 | 8076 | 9418 | 16.62%
60 | 9601000021 | ITEM 60 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 20 HP TO 60 HP | No | 13242.9021 | 12957 | 13637 | 18602 | 36.41%
61 | 9601000022 | ITEM 61 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 60 HP AND ABOVE | No | 16823.7485 | 16615 | 17850 | 23236 | 30.17%
62 | 9601000023 | ITEM 62 | ESTIMATE FOR SINGLE PHASE SERVICE CONNECTION UP TO 6 KW LOAD | No | 2092.8914 | 2030 | 2720 | 3486 | 28.16%
63 | 9601000024 | ITEM 63 | ESTIMATE FOR SINGLE PHASE STREET LIGHT CONNECTION | No | 2245.7269 | 2182 | 2944 | 3716 | 26.22%
64 | 9601000025 | ITEM 64 | ESTIMATE FOR SINGLE PHASE STREET LIGHT FIXTURE | No | 1035.5282 | 1141 | 1238 | 1358 | 9.693%
ARIAL BUNCH CABLE
65 | 9601000049 | ITEM 65 | LT LINE 1PH 2 WIRE USING ABC OF SIZE 1x 35 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES | KM | 185583.2674 | 192965 | 198577 | 253091 | 27.45% | 9601000091
66 | 9601000050 | ITEM 66 | LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 35 SQ MM + 1x 16 SQ MM + 1x 25 SQ MM ON 8 MTR PSC POLES | KM | 256429.2947 | 264497 | 266739 | 366159 | 37.27% | 9601000060
67 |  | ITEM 67 | LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 50 SQ MM + 1x 25 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES | KM |  |  | 312493 | 395203 | 26.47% | 9601000092
68 | 9601000051 | ITEM 68 | 11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 8 MTR PSC POLE | KM | 648522.6509 | 738088 | 769505 | 1014014 | 31.77% | 9601000093
69 | 9601000052 | ITEM 69 | 11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 11 MTR RSJ POLE | KM | 883781.4009 | 975909 | 1083426 | 1459097 | 34.67% | 9601000094
70 |  | ITEM 70 | 11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 10 MTR PSC POLE | KM | New | 813387 | 847669 | 1128392 | 33.12% | 9601000067
MISCELLANEOUS
71 |  | ITEM 71 | SINGLE POLE STRUCTURE WITH 11 KV DO FUSE | NO | New | 21016 | 21192 | 25842 | 21.94% | 9601000070
72 | 9601000048 | ITEM 72 | PROVIDING FANCING AROUND DIST. TRANSFORMER CENTRE | NO | 25165.548 | 25969 | 26508 | 29656 | 11.88%
73 |  | ITEM 73 | REPLACEMENT OF SINGLE PHASE SERVICE CONNECTION BY 4.0 MM2 TWIN CORE ARMOURD CABLE | No | New | 2457 | 1631 | 1946 | 19.31% | 9601000071
74 |  | ITEM 74 | REPLACEMENT OF SINGLE PHASE MMB BY SMC | No | New | 513 | 331 | 398 | 20.24% | 9601000072
75 |  | ITEM 75 | SINGLE PHASE METER REPLACEMENT (UP TO 6 KW LOAD ) | No | New | 958 | 619 | 974 | 57.35% | 9601000073

## INDEX (hidden)
INDEX
Cost Data & Labour Rates
FY 2019-20
Sr.No. | Sheet | Perticular | Page No
1 | ANNEXTURE-A | ITEM WISE COST DATA ( R E/CITY ) FOR THE YEAR 2019-20
2 | ANNEXTURE-B | COST DATA FOR H.T.POWER SUPPLY FOR YEAR 2019-20.

## 1
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 1
RE/CITY COST DATA FOR THE YEAR 2022-23
TAPPING FROM EXISTING POLES FOR 11 KV LINE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | STRAIGHT CROSS ARMS. (1.15 Mtr) | NO. | 2 | 485 | 970
| 36 11 00 0018 | M.S Angle Tapping-11KV FEBRI. 65x65x6x1150MM | NO. | 2 | 485 | 970
2 |  | BRACING FOR SIDE ARM | NO. | 2 | 592 | 1184
| 36 11 00 0031 | Angle Bracing for D.P-65x65x6-750MM | NO. | 2 | 592 | 1184
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 1 | 1194.748 | 1194.748
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 1 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
4 |  | 11KV PIN INSULATORS WITH SPINDLE | SET | 1 | 199.24 | 199.24
| 20 01 00 0006 | (a) 11 KV Pin Insulator | No | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | No | 1 | 0 | 0
199.24
5 |  | 11KV STRAIN INSULATORS WITH H/W | SET | 3 | 416.73 | 1250.19
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
6 |  | M.S. BOLTS OF ASSORTED SIZES &
P.G. CLAMPS OR WITH PREFORMED
|  | FITTINGS. |  |  |  | 501.628
| 15 01 00 0024 | M.S. Bolts & Nuts - 65X16MM | KG | 1.6 | 103.33 | 165.328
| 26 01 00 0027/0028 | P.G. Clamp for Weasel/Rabbit | Nos | 3 | 112.1 | 336.3
501.628
7 |  | CLAMP FOR BRACING AND CROSS ARMS | PAIR | 1 | 182 | 182
| 26 01 00 0049 | Side clamp | Nos. | 2 | 91 | 182
8 |  | COST OF MATERIALS |  |  |  | 5481.806 | 5508.868 | 27.062
9 |  | ADD:3% CONTINGENCIES |  |  |  | 164.4542
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 109.6361
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 109.6361
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 822.2709
13 |  | A |  |  |  | 6687.8033
14 |  | LABOUR CHARGES FOR FIXING
|  | OF CROSS ARMS, BRACING ON LOCATION | NO. | 1 | 363 | 363
15 |  | ERECTION OF STAY SETS. | NO. | 1 | 422 | 422
16 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.15 | 5919 | 887.85
17 |  | LABOUR CHARGES |  |  |  | 1672.85
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 250.9275
19 |  | B |  |  |  | 1923.7775
20 |  | A+B |  |  |  | 8611.5808
|  | TOTAL ESTIMATE |  |  | Say Rs. | 8612

## 2
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 2
RE/CITY COST DATA FOR THE YEAR 2022-23
GUARDING UNDER HT AND LT LINE (SPAN-60 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | GUARDING ANGLE CROSS ARM | NO. | 2 | 857 | 1714
| 26 09 00 0029/ 31 | M.S.Angle 65x65x6mm - 2 Mtr for Guarding Angle cross arm/Guarding channel | No | 2 | 857 | 1714
2 |  | BACK CLAMP | NO. | 2 | 91 | 182
| 26 01 00 0049 | Side clamp | No | 2 | 91 | 182
3 | 01 03 00 0003 | G.I. WIRE 10 SWG | KG. | 2 | 84.19 | 168.38
4 | 01 03 00 0002 | G.I. WIRE NO. 8 | KG. | 14 | 84.19 | 1178.66
5 |  | MISC. ITEMS i.e.BOLTS ,NUTS |  |  |  | 402.664
WASHER,BINDING WIRES.
| 26 14 00 0012 | Eye-bolt | No | 4 | 74 | 296
| 15 01 00 0024 | Bolts & Nuts - 65x16mm | KG | 0.8 | 103.33 | 82.664
| 01 01 00 0003 | Alu.Binding wire | KG | 0.2 | 120 | 24
402.664
6 |  | COST OF MATERIALS |  |  |  | 3645.704
7 |  | ADD:3% CONTINGENCIES |  |  |  | 109.3711
8 |  | ADD:2% STORAGE CHARGES |  |  |  | 72.9141
9 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 72.9141
10 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 546.8556
11 |  | A |  |  |  | 4447.7589
12 |  | LABOUR CHARGES FOR FIXING | NO. | 2 | 363 | 726
OF CROSS ARMS ON LOCATION.
13 |  | PROVIDE GUARDING. | MTR | 60 | 58 | 3480
COMPLETE WITH PAINTING.
14 |  | LABOUR CHARGES |  |  |  | 4206
15 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 630.9
16 |  | B |  |  |  | 4836.9
17 |  | A+B |  |  |  | 9284.6589
|  | TOTAL ESTIMATE |  |  | Say Rs. | 9285

## 3
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 3
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 8 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING A.B SWITCH. | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 91 | 364
A B Switch
| 26 01 00 0049 | Side clamp | No | 4 | 91 | 364
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  |  | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 26 01 00 0027/ 0028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 31185.7464
|  | ADD:3% CONTINGENCIES |  |  |  | 935.5724
|  | ADD:2% STORAGE CHARGES |  |  |  | 623.7149
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 623.7149
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 4677.862
11 |  | A |  |  |  | 38046.6106
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 271 | 542
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/DO Fuse | SET | 1 | 2274 | 2274
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
18 |  | LABOUR CHARGES |  |  |  | 9277.4
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1391.61
20 |  | B |  |  |  | 10669.01
21 |  | A+B |  |  |  | 48715.6206
|  | TOTAL ESTIMATE |  |  | Say Rs. | 48716

## 4
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 4
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 10 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10M/ 200 KG | NO. | 2 | 5136.54 | 10273.08
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING A.B SWITCH. | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 91 | 364
A B Switch
| 26 01 00 0049 | Side clamp | No | 4 | 91 | 364
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  |  | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 26 01 00 0027/ 0028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 35818.4264
|  | ADD:3% CONTINGENCIES |  |  |  | 1074.5528
|  | ADD:2% STORAGE CHARGES |  |  |  | 716.3685
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 716.3685
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 5372.764
11 |  | A |  |  |  | 43698.4802
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 450 | 900
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/DO Fuse | SET | 1 | 4433 | 4433
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
18 |  | LABOUR CHARGES |  |  |  | 11794.4
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1769.16
20 |  | B |  |  |  | 13563.56
21 |  | A+B |  |  |  | 57262.0402
|  | TOTAL ESTIMATE |  |  | Say Rs. | 57262

## 5
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 5
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH On RSJ 9 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 2 | 15077 | 30154 | 3604000002 | Item code change
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING DO Fuse/A.B SWITCH. | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 91 | 1456
| 26 01 00 0049 | Side clamp | No | 16 | 91 | 1456
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  |  | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 26 01 00 0027/ 0028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 56791.3464
|  | ADD:3% CONTINGENCIES |  |  |  | 1703.7404
|  | ADD:2% STORAGE CHARGES |  |  |  | 1135.8269
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1135.8269
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8518.702
11 |  | A |  |  |  | 69285.4426
12 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 271 | 542
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON RSJ POLE WITH
|  | AB SWITCH/DO Fuse | SET | 1 | 2734 | 2734 | 9902020009 | Item code change
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
ITEM 4
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
17 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
18 |  | LABOUR CHARGES |  |  |  | 17787.24
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2668.086
20 |  | B |  |  |  | 20455.326
21 |  | A+B |  |  |  | 89740.7686
|  | TOTAL ESTIMATE |  |  | Say Rs. | 89741

## 6
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 6
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV DOUBLE POLE STRUCTURE WITH HG FUSE (WITHOUT AB SWITCH) On PSC 8 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING DO Fuse | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 91 | 182
FOR DO Fuse.
| 26 01 00 0049 | Side clamp | No | 2 | 91 | 182
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 1161 | 3483
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1787.4144
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 103.33 | 537.316
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 26 01 00 0027/ 0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape for HT Jumpers | Mtr | 20 | 13 | 260
1787.4144
10 |  | COST OF MATERIALS |  |  |  | 23758.6264
11 |  | ADD:3% CONTINGENCIES |  |  |  | 712.7588
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 475.1725
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 475.1725
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 3563.794
15 |  | A |  |  |  | 28985.5242
16 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 271 | 542
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
17 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE,DO Fuse | SET | 1 | 2274 | 2274
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
18 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
19 |  | LABOUR CHARGES |  |  |  | 9277.4
20 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1391.61
21 |  | B |  |  |  | 10669.01
22 |  | A+B |  |  |  | 39654.5342
|  | TOTAL ESTIMATE |  |  | Say Rs. | 39655

## 7
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 7
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH 34 MM2 AAAC CONDUCTOR( SPAN 50 MTR ) ON 8 MTR PSC POLE WITH WIND PRESSURE ZONE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2820.2 | 56404
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 787 | 15740
3 |  | BACK CLAMP FOR FIXING CROSS ARM. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Sideclamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | HT TOP | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | NO. | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 199.24 | 11954.4
| 20 01 00 0006 | (a)11 KV Pin Insulator | No | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | No | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL. | NO. | 12 | 416.73 | 5000.76
WITH H/W & PREFORM FITTING.
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 SIZE. | KM. | 3.09 | 25415 | 78532.35
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4015.6758
CLAMP,BINDINGWIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 103.33 | 1198.628
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.66 | 103.33 | 1618.1478
| 26 01 00 0027 | (c) P.G. Clamp for Weasel | No | 9 | 112.1 | 1008.9
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 10 | 13 | 130
4015.6758
14 |  | COST OF MATERIALS |  |  |  | 189721.0818
15 |  | ADD:3% CONTINGENCIES |  |  |  | 5691.6325
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 3794.4216
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3794.4216
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 28458.1623
19 |  | A |  |  |  | 231459.7198
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 271 | 5420
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 878 | 17560
OF PSC POLE INCLUDING DIGGING.
OF PITS FIXING OF POLES FIXTURE
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 422 | 844
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5919 | 1775.7
28 |  | LABOUR CHARGE |  |  |  | 41170.7
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6175.605
30
30 |  | B |  |  |  | 47346.305
31 |  | A+B |  |  |  | 278806.0248
|  | TOTAL ESTIMATE |  |  | Say Rs. | 278806

## 8
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 8
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2820.2 | 56404
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 787 | 15740
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 199.24 | 11954.4
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 12 | 416.73 | 5000.76
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4146.0891
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 103.33 | 1198.628
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.664 | 103.33 | 1618.5611
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 112.1 | 1008.9
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 20 | 13 | 260
4146.0891
14 |  | COST OF MATERIALS |  |  |  | 234863.5251
15 |  | ADD:3% CONTINGENCIES |  |  |  | 7045.9058
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 4697.2705
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4697.2705
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 35229.5288
19 |  | A |  |  |  | 286533.5006
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 271 | 5420
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 878 | 17560
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 422 | 844
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5919 | 1775.7
28 |  | LABOUR CHARGES |  |  |  | 41170.7
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6175.605
30 |  | B |  |  |  | 47346.305
31 |  | A+B |  |  |  | 333879.8056
|  | TOTAL ESTIMATE |  |  | Say Rs. | 333880

## 9
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 9
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 30 | 2820.2 | 84606
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 787 | 23610
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 199.24 | 17931.6
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 416.73 | 10001.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 7681.2167
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 19 | 103.33 | 1963.27
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 25.99 | 103.33 | 2685.5467
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
7681.2167
14 |  | COST OF MATERIALS |  |  |  | 295480.3087
15 |  | ADD:3% CONTINGENCIES |  |  |  | 8864.4093
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 5909.6062
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5909.6062
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 44322.0463
19 |  | A |  |  |  | 360485.9766
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 30 | 271 | 8130
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 878 | 26340
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 422 | 1688
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
28 |  | LABOUR CHARGES |  |  |  | 60140.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9021.06
30
30 |  | B |  |  |  | 69161.46
31 |  | A+B |  |  |  | 429647.4366
|  | TOTAL ESTIMATE |  |  | Say Rs. | 429647

## 10
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 10
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH DOG CONDUCTOR (SPAN-50 MTR) ON PSC POLE (10 MTR) WITH 11 KV MATERIALS
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 20 | 5136.54 | 102730.8
2 | 26 09 00 0034 | 11 KV V CROSS ARM. | NO. | 20 | 1021 | 20420
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11 KV PIN INSULATOR COMPL. | NO. | 54 | 199.24 | 10758.96
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11 KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 551.73 | 13241.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 135 | 270
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
551.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 73163 | 226073.67
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6008.304
14 |  | COST OF MATERIALS |  |  |  | 399696.646
15 |  | ADD:3% CONTINGENCIES |  |  |  | 11990.8994
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 7993.9329
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7993.9329
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 59954.4969
19 |  | A |  |  |  | 487629.9081
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 271 | 5420
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 2055 | 41100
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 422 | 1688
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
28 |  | LABOUR CHARGES |  |  |  | 67330.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10099.56
30 |  | B |  |  |  | 77429.96
31 |  | A+B |  |  |  | 565059.8681
|  | TOTAL ESTIMATE |  |  | Say Rs. | 565060
5

## 11
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 11
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH DOG CONDUCTOR (SPAN-33 MTR) ON PSC POLE (10 MTR) WITH 11 KV materials
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 30 | 5136.54 | 154096.2
2 | 26 09 00 0034 | 11 KV V CROSS ARM. | NO. | 30 | 1021 | 30630
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11 KV PIN INSULATOR COMPL. | NO. | 90 | 199.24 | 17931.6
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11 KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 551.73 | 13241.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 135 | 270
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
551.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 73163 | 226073.67
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6008.304
14 |  | COST OF MATERIALS |  |  |  | 478476.382
15 |  | ADD:3% CONTINGENCIES |  |  |  | 14354.2915
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 9569.5276
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 9569.5276
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 71771.4573
19 |  | A |  |  |  | 583741.186
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 271 | 8130
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 2055 | 61650
|  | OF RSJ POLE INCLUDING DIGGING. |  |  |  |  | 350
|  | OF PITS,FIXING OF POLES FIXTURE, |  |  |  |  | 7000
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
28 |  | LABOUR CHARGES |  |  |  | 96294.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 14444.16
30 |  | B |  |  |  | 110738.56
31 |  | A+B |  |  |  | 694479.746
|  | TOTAL ESTIMATE |  |  | Say Rs. | 694480
5

## 12
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 12
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH DOG AAAC CONDUCTOR (SPAN-33 MTR) ON RSJ POLE (9 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 30 | 15077 | 452310 | 1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 30 | 12986 | 389580
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 1021 | 30630
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730 | 2 | 26 09 00 0034 | 22KV V CROSS ARM. | NO. | 30 | 720 | 21600
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730 | 3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800 |  | 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400 | 4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400 | 5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488 |  | 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
|  | Material required for1 No. Guy set |  |  |  |  | 6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260 |  |  | Material required for1 No. Guy set
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628 |  | 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74 |  | 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05 |  | 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07 |  | 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200 |  | 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5 |  | 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
[6 empty] | 1194.748 |  | 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6 | [6 empty] | 1057
|  | Material required for 1 No earthing |  |  |  |  | 7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57 |  |  | Material required for 1 No earthing
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65 |  | 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
[6 empty] | 333.22 |  | 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600 | [6 empty] | 262
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600 | 8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800 |  | 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 199.24 | 17931.6
|  | WITH H/W & PREFORM FITTING. |  |  |  |  | 9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
| 20 01 00 0006 | (a11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24 | 10 |  | 22KV PIN INSULATOR COMPL. | NO. | 90 | 0 | 0
| 20 10 00 0010 | (b)11 KV GI Pin | NO. | 1 | 0 | 0 |  |  | WITH H/W & PREFORM FITTING.
[6 empty] | 199.24 |  | 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 1 | 0 | 0
11 |  | 11KV STRAIN INSULATOR COMPL. | [5 empty] | 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 1 | 0 | 0
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 551.73 | 13241.52 | [6 empty] | 0
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 135 | 270 | 11 |  | 22KV STRAIN INSULATOR COMPL.
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73 |  |  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944
551.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 73163 | 226073.67 |  | 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304 |  | 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
|  | CLAMP;BINDING WIRE,TAPS,BOLT, | [10 empty] | 456
|  | NUTS WITH PREFORM FITTING. |  |  |  |  | 12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0 | 13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4 |  |  | CLAMP;BINDING WIRE,TAPS,BOLT,
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108 |  |  | NUTS WITH PREFORM FITTING.
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234 |  | 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
[6 empty] | 6008.304 |  | 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
14 |  | COST OF MATERIALS |  |  |  | 776690.182 |  | 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
15 |  | ADD:3% CONTINGENCIES |  |  |  | 23300.7055 |  | 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 15533.8036 |  | 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 15533.8036 | [6 empty] | 4998
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 116503.5273
19 |  | A |  |  |  | 947562.022 | 14 |  | COST OF MATERIALS |  |  |  | 632061.42
[7 empty] | 19 |  | A |  |  |  | 632061.42
[9 empty] | ADD:3% CONTINGENCIES |  |  |  | 18961.8426
[9 empty] | ADD:2% STORAGE CHARGES |  |  |  | 12641.2284
[9 empty] | ADD:2% TRANSPORTATION & MISC. |  |  |  | 12641.2284
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475 |  |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 94809.213
21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 271 | 8130
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600 |  |  | Total ….A |  |  |  | 771114.9324
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1395 | 41850
|  | OF RSJ POLE INCLUDING DIGGING. |  |  |  |  | 20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
|  | OF PITS,FIXING OF POLES FIXTURE, |  |  |  |  | 21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 230 | 6900
|  | INSULATOR & PAINTING STEEL POLE |  |  |  |  | 22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 3668 | 11004 | 23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1180 | 35400
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 422 | 1688 |  |  | OF RSJ POLE INCLUDING DIGGING.
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580 |  |  | OF PITS,FIXING OF POLES FIXTURE,
|  | EARTHING WITH SALT & COAL. |  |  |  |  | 24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 2900 | 8700
27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5919 | 126074.7
28 |  | LABOUR CHARGES |  |  |  | 204401.7 | 25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 335 | 2010
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 30660.255
[7 empty] | 26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 370 | 11100
30 |  | B |  |  |  | 235061.955 | 27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5900 | 125670
31 |  | A+B |  |  |  | 1182623.977
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1182624 | 28 |  | LABOUR CHARGES |  |  |  | 190755
[7 empty] | 29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 28613.25
30
[7 empty] | 31 |  | B |  |  |  | 219368.25
[7 empty] | 32 |  | Sub Total(A+B) |  |  |  | 990483.1824
[9 empty] | Total Estimate |  |  | Say Rs. | 990483.1824

## 13
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 13
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-50 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 20 | 5136.54 | 102730.8
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 787 | 15740
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 199.24 | 11954.4
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 12 | 416.73 | 5000.76
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4016.0891
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 103.33 | 1198.628
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.664 | 103.33 | 1618.5611
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 112.1 | 1008.9
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 10 | 13 | 130
4016.0891
14 |  | COST OF MATERIALS |  |  |  | 281060.3251
15 |  | ADD:3% CONTINGENCIES |  |  |  | 8431.8098
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 5621.2065
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5621.2065
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 42159.0488
19 |  | A |  |  |  | 342893.5966
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 450 | 9000
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 2055 | 41100
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 422 | 844
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5919 | 1775.7
28 |  | LABOUR CHARGES |  |  |  | 68290.7
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10243.605
30 |  | B |  |  |  | 78534.305
31 |  | A+B |  |  |  | 421427.9016
|  | TOTAL ESTIMATE |  |  | Say Rs. | 421428

## 14
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 14
RE/CITY COST DATA FOR THE YEAR 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 30 | 5136.54 | 154096.2
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 787 | 23610
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 199.24 | 17931.6
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 416.73 | 10001.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4016.0891
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 103.33 | 1198.628
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.664 | 103.33 | 1618.5611
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 112.1 | 1008.9
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 10 | 13 | 130
4016.0891
14 |  | COST OF MATERIALS |  |  |  | 361305.3811
15 |  | ADD:3% CONTINGENCIES |  |  |  | 10839.1614
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 7226.1076
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7226.1076
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 54195.8072
19 |  | A |  |  |  | 440792.565
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 30 | 450 | 13500
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 2055 | 61650
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 422 | 1688
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5919 | 1775.7
28 |  | LABOUR CHARGES |  |  |  | 99044.7
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 14856.705
30
30 |  | B |  |  |  | 113901.405
31 |  | A+B |  |  |  | 554693.97
|  | TOTAL ESTIMATE |  |  | Say Rs. | 554694

## 15
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 15
RE/CITY COST DATA FOR THE YEAR 2022-23
UNDER GROUND RAILWAY CROSSING (DOUBLE TRACK- BROAD GAUGE) FOR 11 KV SYSTEM
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 36 04 00 0001 | RSJ 116*100 MM 9 MTR. | NO. | 4 | 15077 | 60308
2 | 26 09 00 0034 | V CROSS ARMS 11KV | NO. | 4 | 787 | 3148
3 |  | STRAIN INSULATOR 11 KV WITH H/W | SET | 6 | 416.73 | 2500.38
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
4 | 04 05 00 0009 | 11 KVXLPE CABLE 3 CORE 185 mm2 SIZE.(Double CKT) | MTR | 230 | 1039.58 | 239103.4
5 |  | ANTI-CLIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | No | 2 | 120 | 240
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
8 |  | SUNDRY MATERIAL SUCH AS |  |  |  | 1723.912
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6.4 | 103.33 | 661.312
| 19 05 00 0006 | (b) HT Binding Tape | Mtr | 30 | 13 | 390
| 26 01 00 0027/0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
1723.912
9 |  | COST OF MATERIALS |  |  |  | 314312.18
10 |  | ADD:3% CONTINGENCIES |  |  |  | 9429.3654
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 6286.2436
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 6286.2436
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 47146.827
14 |  | A |  |  |  | 383460.8596
15 |  | LABOUR CHARGES FOR COMPLETE |  |  | ----LS---- | 350000
WORK OF CROSSING
(INCLUDING LAYING, JOINTING, INSERTATIOIN OF 150MM DIA C. I. PIPE UNDER RAILWAY TRACK USING HORIZONTAL AUGER GUIDED BORING BY PUSH THROUGH METHOD; INSERTATION OF C. I. PIPE IN SIDE RAILWAY BOUNDRY BY CUT AND FILL METHOD; PROVIDING AND SUPPLY OF 150MM DIA C. I. PIPE; LAYING OF 11KV XLPE CABLE IN SIDE C. I. PIPE; PROVIDING SUPPLY AND FIXING 185MM2 CABLE BOX, TERMINATION KIT; PROVIDING PAINTING, FABRICATION AND FIXING OF CABLE MARKER; PROVIDING AND FIXING OF G. I, PIPE ON ERECTED STRUCTURE FOR MECHANICAL PROTECTION OF XLPE CABLE & PROVIDING EARTHING AS PER RAILWAY AUTHORITY ETC.) THE FOLLOWING ITEMS ARE COVERED IN THE SCOPE OF SUPPLIER/CONTRACTOR. LENGTH OF CI PIPE, EARTHING, ITS INSTALLATION EVERYTHING BETWEEN TWO END TERMINATION ACROSS THE RAILWAY TRACK SHALL BE ACCORDING TO DRAWING APPROVED BY CONCERN RAILWAY AUTHORITY. CABLE WILL BE CARTED FROM STORE TO SITE BY CONTRACTOR. ONLY CABLE WILL BE PROVIDED BY UGVCL.
16 |  | CARTING OF RSJ POLE AT DEST. | NO. | 2 | 271 | 542
17 |  | CARTING OF LINE MATERIAL AT |  |  | ----LS---- | 600
WORK SITE
18 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 2.26 | 5919 | 13376.94
19 |  | LABOUR CHARGES |  |  |  | 364518.94
20 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 54677.841
21
21 |  | B |  |  |  | 419196.781
22 |  | A+B |  |  |  | 802657.6406
|  | TOTAL ESTIMATE |  |  | Say Rs. | 802658

## 16
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 16
RE/CITY COST DATA FOR THE YEAR 2022-23
RIVER CROSSING (11KV) on 10 MTR PSC POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 Meter 200 KG | NO. | 4 | 5136.54 | 20546.16
2 |  | TOP CROSS ARMS FOR TERMINATING | NO. | 4 | 1180 | 4720
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750 mm for top cross arm for terminating line | No | 4 | 1180 | 4720
3 |  | BRACING FOR DOUBLE POLE STRUCTURE | SET | 2 | 4720 | 9440
|  | ( 4 angles per set) |  | 8 | 1180 | 9440
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV
4 |  | 11 KV STRAIN INSULATOR H/W WITH | SET | 12 | 416.73 | 5000.76
PREFORMED FITTING
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
5 |  | ANTI-CLIMBING DEVICES. | NO. | 4 | 120 | 480
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 4 | 120 | 480
30.192
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 4 | 60 | 240
7 |  | EARTHING OF D.P. STRUCTURE | NO. | 4 | 486.84 | 1947.36
Material required for 1 No. Pipe Type earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 1 Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (e) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (f) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | GUY SET WITH PREFORMED FITTING | NO. | 8 | 1194.748 | 9557.984
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
9 |  | SUNDRY MATERIAL SUCH AS BOLT & |  |  |  | 1837.1674
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 103.33 | 495.984
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 4.98 | 103.33 | 514.5834
| 26 01 00 0027/ 0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 19 05 00 0006 | (d) HT Tape for binding | Mtr | 10 | 13 | 130
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.2 | 120 | 24
1837.1674
10 |  | COST OF MATERIALS |  |  |  | 53769.4314
11 |  | ADD:3% CONTINGENCIES |  |  |  | 1613.0829
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 1075.3886
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1075.3886
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8065.4147
15 |  | A |  |  |  | 65598.7063
16 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE . | NO. | 2 | 4433 | 8866
17 |  | INSTALLATION OF EARTHING COIL | NO. | 4 | 486 | 1944
PLATE TYPE WITH SALT &COAL
ITEM 14
18 |  | PROVIDING GUY SET COMP.WITH | NO. | 8 | 422 | 3376
ALL ACCESSORES &FITTING
19 |  | CARTING OF POLE AT DEST. | NO. | 4 | 450 | 1800
20 |  | CARTING OF MATERIAL AT WORK SITE |  |  | ----LS---- | 600
21 |  | CONCRETING OF GUY & PSC POLES WITH MATERIAL(1:2:4) | CMT | 1.2 | 5919 | 7102.8
22 |  | LABOUR CHARGES.. |  |  |  | 23688.8
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3553.32
24 |  | B |  |  |  | 27242.12
25 |  | A+B |  |  |  | 92840.8263
|  | TOTAL ESTIMATE |  |  | Say Rs. | 92841

## 17
UTTAR GUJARAT VIJ COMPANY LIMITED | [5 empty] | COST DATA
ITEM 17
RE/CITY COST DATA FOR THE YEAR 2022-23
25 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2820.2 | 2820.2
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 3822
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 113 | 113
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 1016 | 1016
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 621 | 1242
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 272 | 544
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing DO Fuse | No | 1 | 621 | 621
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing DO Fuse. | No | 2 | 143 | 286
3822
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 1 | 7729 | 7729
10 |  | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 5 | 71.38 | 356.9
11 |  | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV.(Amorphos) | NO. | 1 | 77999 | 77999
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 1412.8186
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 103.33 | 619.98
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 103.33 | 146.7286
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 91 | 546
1412.8186
15 |  | COST OF MATERIALS |  |  |  | 108223.3346
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3246.7
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2164.4667
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2164.4667
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 16233.5002
20 |  | A |  |  |  | 132032.4682
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,DO FuseS,
|  | DIST.BOX ETC. | NO. | 1 | 3244 | 3244
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 422 | 844
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 271 | 271
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5919 | 4320.87
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
28 |  | LABOUR CHARGES |  |  |  | 11287.87
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1693.1805
31 |  | B |  |  |  | 12981.0505
32 |  | A+B |  |  |  | 145013.5187
|  | TOTAL ESTIMATE |  |  | Say Rs. | 145014
S

## 18
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 18
RE/CITY COST DATA FOR THE YEAR 2022-23
16 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2820.2 | 2820.2
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 3822
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 113 | 113
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 1016 | 1016
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 621 | 1242
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 272 | 544
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing DO Fuse | No | 1 | 621 | 621
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing DO Fuse. | No | 2 | 143 | 286
3822
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 1 | 7729 | 7729
10 |  | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 5 | 71.38 | 356.9
11 |  | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 16 KVA 11KV/0.433KV. | NO. | 1 | 64900 | 64900
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 1412.8186
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 103.33 | 619.98
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 103.33 | 146.7286
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 91 | 546
1412.8186
15 |  | COST OF MATERIALS |  |  |  | 95124.3346
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2853.73
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1902.4867
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1902.4867
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 14268.6502
20 |  | A |  |  |  | 116051.6882
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 3244 | 3244
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 422 | 844
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 271 | 271
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5919 | 4320.87
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
28 |  | LABOUR CHARGES |  |  |  | 11287.87
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1693.1805
30 |  | B |  |  |  | 12981.0505
31 |  | A+B |  |  |  | 129032.7387
|  | TOTAL ESTIMATE |  |  | Say Rs. | 129033

## 19
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 19
RE/CITY COST DATA FOR THE YEAR 2022-23
10 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2820.2 | 2820.2
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 3822
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 113 | 113
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 1016 | 1016
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 621 | 1242
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 272 | 544
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing HG Fuse | No | 1 | 621 | 621
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing HG Fuse. | No | 2 | 143 | 286
3822
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 1 | 7729 | 7729
10 |  | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 5 | 71.38 | 356.9
11 |  | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV. | NO. | 1 | 55700 | 55700
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 1412.8186
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 103.33 | 619.98
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 103.33 | 146.7286
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 91 | 546
1412.8186
15 |  | COST OF MATERIALS |  |  |  | 85924.3346
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2577.73
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1718.4867
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1718.4867
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 12888.6502
20 |  | A |  |  |  | 104827.6882
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 3244 | 3244
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 422 | 844
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 271 | 271
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5919 | 4320.87
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES |  |  |  | 11287.87
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1693.1805
30 |  | B |  |  |  | 12981.0505
31 |  | A+B |  |  |  | 117808.7387
|  | TOTAL ESTIMATE |  |  | Say Rs. | 117809

## 20
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 20
RE/CITY COST DATA FOR THE YEAR 2022-23
5 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2820.2 | 2820.2
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 3822
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 113 | 113
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 1016 | 1016
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 621 | 1242
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 272 | 544
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing HG Fuse | No | 1 | 621 | 621
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing HG Fuse. | No | 2 | 143 | 286
3822
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 2 | 1161 | 2322
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 2 | 519 | 1038
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 1 | 120 | 120
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 |  |  |  | 7729 | 0
10 |  | PVC INSULATED & SHEATHED 4 MM2 | MTR | 5 | 11 | 55
2 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 2C * 4mm2 LT PVC Cable | MTR | 5 | 11 | 55
11 |  | -DO- 4 MM2 OUT GOING SIDE. | MTR | 30 | 11 | 330
| 04 01 00 0035 | 2 C x 4mm2 LT PVC Cable | MTR | 30 | 11 | 330
12 | 44 06 02 0002 | X'MER 5 KVA | NO. | 1 | 50000 | 50000
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 1184.6 | 1184.6
| 1601000073 | (i) 5-30 A Static Meter | NO | 1 | 744 | 744
| 1607000009 | (ii) 1-ph SMB | NO | 1 | 258.6 | 258.6
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
1184.6
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 1412.8186
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 103.33 | 619.98
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 103.33 | 146.7286
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 91 | 546
1412.8186
15 |  | COST OF MATERIALS |  |  |  | 67074.6346
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2012.239
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1341.4927
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1341.4927
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 10061.1952
20 |  | A |  |  |  | 81831.0542
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 3244 | 3244
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 422 | 844
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 271 | 271
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5919 | 4320.87
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES |  |  |  | 11287.87
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1693.1805
30 |  | B |  |  |  | 12981.0505
31 |  | A+B |  |  |  | 94812.1047
|  | TOTAL ESTIMATE |  |  | Say Rs. | 94812

## 21
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 21
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 9956
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 321 | 1284
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9956
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 7729 | 7729
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV.(LEVEL 2) | NO. | 1 | 55700 | 55700
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 3429.8345
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 103.33 | 574.5148
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3429.8345
15 |  | COST OF MATERIALS |  |  |  | 99285.0465
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2978.5514
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1985.7009
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1985.7009
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 14892.757
20 |  | A |  |  |  | 121127.7567
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 15203.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2280.51
30 |  | B |  |  |  | 17483.91
31 |  | A+B |  |  |  | 138611.6667
|  | TOTAL ESTIMATE |  |  | Say Rs. | 138612

## 22
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 22
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 9956
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 321 | 1284
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9956
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 7729 | 7729
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0008 | X'MER 16 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 64900 | 64900
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 3429.8345
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 103.33 | 574.5148
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/ 0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3429.8345
15 |  | COST OF MATERIALS |  |  |  | 108485.0465
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3254.5514
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2169.7009
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2169.7009
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 16272.757
20 |  | A |  |  |  | 132351.7567
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 350
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 350
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 14753.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2213.01
30 |  | B |  |  |  | 16966.41
31 |  | A+B |  |  |  | 149318.1667
|  | TOTAL ESTIMATE |  |  | Say Rs. | 149318

## 23
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 23
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 9944
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9944
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 7729 | 7729
10 | 04 01 00 0035 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0035 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 77999 | 77999
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 3223.1745
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/ 0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3223.1745
15 |  | COST OF MATERIALS |  |  |  | 121365.3865
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3640.9616
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2427.3077
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2427.3077
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 18204.808
20 |  | A |  |  |  | 148065.7715
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 15203.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2280.51
30 |  | B |  |  |  | 17483.91
31 |  | A+B |  |  |  | 165549.6815
|  | TOTAL ESTIMATE |  |  | Say Rs. | 165550

## 24
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 24
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9944
OF FUSES 11KV.
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9944
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 486.84 | 1460.52
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | 63KVA L.T. DIST. BOX | NO. | 1 | 9652 | 9652
10 |  | PVC INSULATED & SHEATHED 70 MM2 | MTR | 5 | 234.5 | 1172.5
| 04 01 00 0004 | 3.5 Cx 70mm2 LT PVC Cable | MTR | 5 | 234.5 | 1172.5
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 30 | 108.97 | 3269.1
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 30 | 108.97 | 3269.1
12 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV.LEVEL-2) | NO. | 1 | 123800 | 123800
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 4759 | 4759
| 1601000069 | (i) 100/5 A Static Meter . | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000046 | (iv) Ring Type LT CT-100/5 A | SET | 1 | 1695 | 1695
4759
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3286.1445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 18 | 54
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 5 | 10
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3286.1445
15 |  | COST OF MATERIALS |  |  |  | 173162.6565
16 |  | ADD:3% CONTINGENCIES |  |  |  | 5194.8797
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 3463.2531
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3463.2531
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 25974.3985
20 |  | A |  |  |  | 211258.4409
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 15203.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2280.51
30
30 |  | B |  |  |  | 17483.91
31 |  | A+B |  |  |  | 228742.3509
|  | TOTAL ESTIMATE |  |  | Say Rs. | 228742

## 25
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 25
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 12685 | 12685
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 180.89 | 5426.7
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 180.89 | 5426.7
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 160800 | 160800
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3390.1645
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/ 0028 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 4 | 12
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 91 | 1092
3390.1645
15 |  | COST OF MATERIALS |  |  |  | 220419.3165
16 |  | ADD:3% CONTINGENCIES |  |  |  | 6612.5795
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 4408.3863
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4408.3863
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 33062.8975
20 |  | A |  |  |  | 268911.5661
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 15203.4
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2280.51
30 |  | B |  |  |  | 17483.91
31 |  | A+B |  |  |  | 286395.4761
|  | TOTAL ESTIMATE |  |  | Say Rs. | 286395

## 26
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 26
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 15077 | 30154
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 12685 | 12685
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 180.89 | 5426.7
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 180.89 | 5426.7
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. (LEVEL-2) | NO. | 1 | 160800 | 160800
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 5081.6445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 103.33 | 1033.3
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 91 | 2184
5081.6445
15 |  | COST OF MATERIALS |  |  |  | 246624.3965
16 |  | ADD:3% CONTINGENCIES |  |  |  | 7398.7319
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 4932.4879
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4932.4879
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 36993.6595
20 |  | A |  |  |  | 300881.7637
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 24028.24
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3604.236
30 |  | B |  |  |  | 27632.476
31 |  | A+B |  |  |  | 328514.2397
|  | TOTAL ESTIMATE |  |  | Say Rs. | 328514

## 27
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 27
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 15077 | 30154
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 200 KVA L.T. DIST. BOX | NO. | 1 | 82156 | 82156
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 70 MM2 OUT GOING SIDE. | MTR | 30 | 234.5 | 7035
| 04 01 00 0003 | 3.5 C x 70mm2 LT PVC Cable | MTR | 30 | 234.5 | 7035
12 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 427000 | 427000
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 5081.6445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 103.33 | 1033.3
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-20 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 91 | 2184
5081.6445
15 |  | COST OF MATERIALS |  |  |  | 583903.6965
16 |  | ADD:3% CONTINGENCIES |  |  |  | 17517.1109
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 11678.0739
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11678.0739
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 87585.5545
20 |  | A |  |  |  | 712362.5097
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
28 |  | LABOUR CHARGES… |  |  |  | 24028.24
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3604.236
30 |  | B |  |  |  | 27632.476
31 |  | A+B |  |  |  | 739994.9857
|  | TOTAL ESTIMATE |  |  | Say Rs. | 739995

## 28
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 28
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 9956
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 321 | 1284
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9956
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 7729 | 7729
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV. | NO. | 1 | 55700 | 55700
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 3429.8345
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 103.33 | 574.5148
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3429.8345
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 115170.9175
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3455.1275
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2303.4183
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2303.4183
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 17275.6376
20 |  | A |  |  |  | 140508.5193
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.28314 | 5919 | 1675.8873
28 |  | LABOUR CHARGES… |  |  |  | 23042.2873
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3456.3431
30 |  | B |  |  |  | 26498.6304
31 |  | A+B |  |  |  | 167007.1498
|  | TOTAL ESTIMATE |  |  | Say Rs. | 167007

## 29
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 29
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 9956
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 321 | 1284
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9956
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 7729 | 7729
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0008 | X'MER 16 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 64900 | 64900
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 3429.8345
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 103.33 | 574.5148
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3429.8345
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 124370.9175
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3731.1275
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2487.4183
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2487.4183
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 18655.6376
20 |  | A |  |  |  | 151732.5193
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 350
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 350
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 22455.34
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3368.301
30 |  | B |  |  |  | 25823.641
31 |  | A+B |  |  |  | 177556.1603
|  | TOTAL ESTIMATE |  |  | Say Rs. | 177556

## 30
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 30
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 9944
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9944
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 7729 | 7729
10 | 04 01 00 0035 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 71.38 | 356.9
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0035 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 71.38 | 2141.4
12 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 77999 | 77999
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2692 | 2692
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1868 | 1868
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
2692
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 3223.1745
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 18 | 54
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.85 | 3.7
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 4 | 12
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.85 | 1.85
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3223.1745
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 137251.2575
16 |  | ADD:3% CONTINGENCIES |  |  |  | 4117.5377
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2745.0251
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2745.0251
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 20587.6886
20 |  | A |  |  |  | 167446.5341
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 22905.34
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3435.801
30 |  | B |  |  |  | 26341.141
31 |  | A+B |  |  |  | 193787.6751
|  | TOTAL ESTIMATE |  |  | Say Rs. | 193788

## 31
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 31
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9944
OF FUSES 11KV.
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 1180 | 7080
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
9944
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 486.84 | 1460.52
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | 63KVA L.T. DIST. BOX | NO. | 1 | 9652 | 9652
10 |  | PVC INSULATED & SHEATHED 70 MM2 | MTR | 5 | 234.5 | 1172.5
| 04 01 00 0004 | 3.5 Cx 70mm2 LT PVC Cable | MTR | 5 | 234.5 | 1172.5
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 30 | 108.97 | 3269.1
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 30 | 108.97 | 3269.1
12 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 123800 | 123800
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 4759 | 4759
| 1601000069 | (i) 100/5 A Static Meter . | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000046 | (iv) Ring Type LT CT-100/5 A | SET | 1 | 1695 | 1695
4759
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3286.1445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 18 | 54
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 5 | 10
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3286.1445
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 189048.5275
16 |  | ADD:3% CONTINGENCIES |  |  |  | 5671.4558
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 3780.9706
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3780.9706
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 28357.2791
20 |  | A |  |  |  | 230639.2036
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (LumSum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 22905.34
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3435.801
30 |  | B |  |  |  | 26341.141
31 |  | A+B |  |  |  | 256980.3446
|  | TOTAL ESTIMATE |  |  | Say Rs. | 256980

## 32
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 32
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 12685 | 12685
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 180.89 | 5426.7
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 180.89 | 5426.7
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 160800 | 160800
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3390.1645
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 4 | 12
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 91 | 1092
3390.1645
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 236305.1875
16 |  | ADD:3% CONTINGENCIES |  |  |  | 7089.1556
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 4726.1038
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4726.1038
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 35445.7781
20 |  | A |  |  |  | 288292.3287
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 22905.34
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3435.801
30 |  | B |  |  |  | 26341.141
31 |  | A+B |  |  |  | 314633.4697
|  | TOTAL ESTIMATE |  |  | Say Rs. | 314633

## 33
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 33
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 15077 | 30154
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 12685 | 12685
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 180.89 | 5426.7
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 180.89 | 5426.7
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 160800 | 160800
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 5081.6445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 103.33 | 1033.3
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 91 | 2184
5081.6445
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 262510.2675
16 |  | ADD:3% CONTINGENCIES |  |  |  | 7875.308
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 5250.2054
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5250.2054
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 39376.5401
20 |  | A |  |  |  | 320262.5264 | 2800
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 31730.18
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 4759.527
30 |  | B |  |  |  | 36489.707
31 |  | A+B |  |  |  | 356752.2333
|  | TOTAL ESTIMATE |  |  | Say Rs. | 356752

## 34
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 34
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 15077 | 30154
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 200 KVA L.T. DIST. BOX | NO. | 1 | 82156 | 82156
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 70 MM2 OUT GOING SIDE. | MTR | 30 | 234.5 | 7035
| 04 01 00 0003 | 3.5 C x 70mm2 LT PVC Cable | MTR | 30 | 234.5 | 7035
12 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 427000 | 427000
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 5081.6445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 103.33 | 1033.3
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-20 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 91 | 2184
5081.6445
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 599789.5675
16 |  | ADD:3% CONTINGENCIES |  |  |  | 17993.687
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 11995.7913
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11995.7913
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 89968.4351
20 |  | A |  |  |  | 731743.2723
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 31730.18
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 4759.527
30 |  | B |  |  |  | 36489.707
31 |  | A+B |  |  |  | 768232.9794
|  | TOTAL ESTIMATE |  |  | Say Rs. | 768233

## 35
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 33
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON 10 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 2 | 5136.54 | 10273.08
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 200 KVA L.T. DIST. BOX | NO. | 1 | 82156 | 82156
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 532.98 | 2664.9
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 532.98 | 2664.9
11 |  | -DO- BUT 70 MM2 OUT GOING SIDE. | MTR | 30 | 234.5 | 7035
| 04 01 00 0003 | 3.5 C x 70mm2 LT PVC Cable | MTR | 30 | 234.5 | 7035
12 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 427000 | 427000
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 3952.64 | 3952.64
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 888.64 | 888.64
3952.64
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 5081.6445
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 103.33 | 1033.3
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 91 | 2184
5081.6445
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
15 |  | COST OF MATERIALS |  |  |  | 579908.6475
16 |  | ADD:3% CONTINGENCIES |  |  |  | 17397.2594
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 11598.173
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11598.173
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 86986.2971
20 |  | A |  |  |  | 707488.55
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6900 | 6900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 271 | 542
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
28 |  | LABOUR CHARGES… |  |  |  | 31041.18
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 4656.177
30 |  | B |  |  |  | 35697.357
31 |  | A+B |  |  |  | 743185.9069
|  | TOTAL ESTIMATE |  |  | Say Rs. | 743186

## 36
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 36
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV 500 KVA DIST. TRANSFORMER CENTRE ON PLINTH
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 15077 | 30154
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 8832
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 2750 mm | NO | 2 | 1850 | 3700
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 1180 | 2360
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 0 | 318 | 0
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
8832
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 500 KVA L.T. DIST. BOX | NO. | 1 | 183748 | 183748
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 15 | 532.98 | 7994.7
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 15 | 532.98 | 7994.7
11 |  | -DO- BUT 150 MM2 OUT GOING SIDE. | MTR | 45 | 532.98 | 23984.1
| 04 01 00 0003 | 3.5 C x 150 mm2 LT PVC Cable | MTR | 45 | 532.98 | 23984.1
12 | 44 06 02 0023 | X'MER 500 KVA 11KV/0.433KV. | NO. | 1 | 1103637.48 | 1103637.48
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 2 | 3624 | 7248
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 2240 | 2240
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 642 | 642
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
| 1608000049 | (iv) Ring Type LT CT-900/5A | SET | 1 | 560 | 560
3624
14 | 614000011 | 11 KV R M U(SF-6) | NO | 1 | 482474 | 482474
15 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 4552.3165
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 8.4 | 103.33 | 867.972
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-20 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 20 | 91 | 1820
4552.3165
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 15885.871
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 59.6 | 3723.808
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 59.6 | 6983.928
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 49.62 | 56 | 2778.72
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 84.19 | 2399.415
15885.871
16 |  | COST OF MATERIALS |  |  |  | 1880149.9795
17 |  | ADD:3% CONTINGENCIES |  |  |  | 56404.4994
18 |  | ADD:2% STORAGE CHARGES |  |  |  | 37602.9996
19 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 37602.9996
20 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 282022.4969
21 |  | A |  |  |  | 2293782.975
22 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
23 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
24 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
25 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 271 | 542
26 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
27 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
28 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | PLINTH (3.34*3.34*1.5MTR) FOR MOUNTING X-MER |  |  | ---LS--- | 65715.44
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5919 | 1538.94
29 |  | LABOUR CHARGES… |  |  |  | 97445.62
30 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 14616.843
31 |  | B |  |  |  | 112062.463
32 |  | A+B |  |  |  | 2405845.438
|  | TOTAL ESTIMATE |  |  | Say Rs. | 2405845

## 37SDT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 37
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER- SDT - 24 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING |  |  |  | 17132.52
|  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
|  | (e) C.I. Earthing pipe 100 mm dia,13 mm thick | No. | 2 | 6136 | 12272
|  | (f) GI Earthing strip (50x6mm) | Kg. | 50 | 68 | 3400
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 22232
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA) | No. | 1 | 10920 | 10920
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
10 | 44 06 02 0023 | 11 KVSPECIAL DESIGNED TRANSFORMER- SDT 24 AMP. | NO. | 1 | 112000 | 112000
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3390.1645
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 4 | 12
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 91 | 1092
3390.1645
12 |  | COST OF MATERIALS |  |  |  | 188922.0765
13 |  | ADD:3% CONTINGENCIES |  |  |  | 5667.6623
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 3778.4415
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3778.4415
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 28338.3115
17 |  | A |  |  |  | 230484.9333
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 6814 | 6814
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
20 |  | ERECTION OF EARTHING CHAMBER | NO. | 2 | 2300 | 4600
EXCAVATION OF EART PIT SALT, CHARCOAL & BENTONITE
21 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
22 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
23 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
24 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
25 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
26 |  | INSTALLATION OF IDMT RELAY, CT COIL |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
27 |  | LABOUR CHARGES… |  |  |  | 21903.4
28 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3285.51
29 |  | B |  |  |  | 25188.91
30 |  | A+B |  |  |  | 255673.8433
|  | TOTAL ESTIMATE |  |  | Say Rs. | 255674

## 38SDT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 38
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER - SDT- 30 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING |  |  |  | 17132.52
|  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
|  | (e) C.I. Earthing pipe 100 mm dia,13 mm thick | No. | 2 | 6136 | 12272
|  | (f) GI Earthing strip (50x6mm) | Kg. | 50 | 68 | 3400
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 22232
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA) | No. | 1 | 10920 | 10920
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
10 | 44 06 02 0023 | 11 KV SPECIAL DESIGNED TRANSFORMER-SDT 30 AMP. | NO. | 1 | 135000 | 135000
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3390.1645
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.76 | 13.68
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 4 | 12
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 91 | 1092
3390.1645
12 |  | COST OF MATERIALS |  |  |  | 211922.0765
13 |  | ADD:3% CONTINGENCIES |  |  |  | 6357.6623
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 4238.4415
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4238.4415
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 31788.3115
17 |  | A |  |  |  | 258544.9333
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 6814 | 6814
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
20 |  | ERECTION OF EARTHING CHAMBER | NO. | 2 | 2300 | 4600
EXCAVATION OF EART PIT SALT, CHARCOAL & BENTONITE
21 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
22 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
23 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
24 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
25 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
26 |  | INSTALLATION OF IDMT RELAY, CT COIL |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
27 |  | LABOUR CHARGES… |  |  |  | 21903.4
28 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3285.51
29 |  | B |  |  |  | 25188.91
30 |  | A+B |  |  |  | 283733.8433
|  | TOTAL ESTIMATE |  |  | Say Rs. | 283734

## 39PAT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 39
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 24.7 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING FOR POLE PAT BODY & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 22232
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA, 5P10) | No. | 1 | 10920 | 10920
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
10 | 44 06 02 0023 | 11 KV PILOT ADVANCE TRANSFORMER - PAT 24.7 AMP. | NO. | 1 | 190635 | 190635
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3123.0645
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 91 | 1092
3123.0645
12 |  | COST OF MATERIALS |  |  |  | 251617.9765
13 |  | ADD:3% CONTINGENCIES |  |  |  | 7548.5393
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 5032.3595
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5032.3595
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 37742.6965
17 |  | A |  |  |  | 306973.9313
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 6814 | 6814
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
20 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
21 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
22 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
23 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
24 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
25 |  | INSTALLATION OF IDMT RELAY, CT |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
26 |  | LABOUR CHARGES… |  |  |  | 17303.4
27 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2595.51
28 |  | B |  |  |  | 19898.91
29 |  | A+B |  |  |  | 326872.8413
|  | TOTAL ESTIMATE |  |  | Say Rs. | 326873

## 40PAT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 40
RE/CITY COST DATA FOR THE YEAR 2022-23
11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 54 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 14220
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 1180 | 1180
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
14220
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING FOR POLE PAT BODY & | NO. | 3 | 486.84 | 1460.52
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 33152
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA, 5P10) | No. | 2 | 10920 | 21840
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
10 | 44 06 02 0023 | 11 KV PILOT ADVANCE TRANSFORMER- PAT 54 AMP. | NO. | 1 | 278298 | 278298
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3123.0645
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 112.1 | 672.6
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 91 | 1092
3123.0645
12 |  | COST OF MATERIALS |  |  |  | 350200.9765
13 |  | ADD:3% CONTINGENCIES |  |  |  | 10506.0293
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 7004.0195
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7004.0195
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 52530.1465
17 |  | A |  |  |  | 427245.1913
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 6814 | 6814
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
20 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
21 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
22 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
23 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
24 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
25 |  | INSTALLATION OF IDMT RELAY, CT COIL |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
26 |  | LABOUR CHARGES… |  |  |  | 17303.4
27 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2595.51
28 |  | B |  |  |  | 19898.91
29 |  | A+B |  |  |  | 447144.1013
|  | TOTAL ESTIMATE |  |  | Say Rs. | 447144

## 41
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 41
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 1 PH 2 WIRE USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2820.2 | 56404
2 |  | GUY SETS WITH PREFORMED FITTING. | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 40 | 116.46 | 4658.4
WITH FITTING VIZ. U CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | ALL ALU. ALLOY CONDUCTOR 34MM2 SIZE | KM. | 2.06 | 25415 | 52354.9
OF PHASES, NEUTRAL AND ST. LIGHT
| 01 02 00 0031 | ALL ALU. ALLOY CONDUCTOR 34MM2 | KM | 2.06 | 25415 | 52354.9
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 2679.4112
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2.4 | 103.33 | 247.992
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 14.24 | 103.33 | 1471.4192
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 1 | 120 | 120
| 2615 00 0001/2 | (d) Line spacers for 2 wire line | NO | 40 | 21 | 840
|  | (Considering 2 spacers / span) |  |  |  | 2679.4112
7 |  | COST OF MATERIALS |  |  |  | 129271.5192
8 |  | ADD:3% CONTINGENCIES |  |  |  | 3878.1456
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 2585.4304
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2585.4304
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 19390.7279
12 |  | A |  |  |  | 157711.2534
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF MATERIALS ON TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 20 | 878 | 17560
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 2 | 1592 | 3184
18 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
SALT EARTHING WITH AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 40 | 11 | 440
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES… |  |  |  | 45258.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6788.715
24 |  | B |  |  |  | 52046.815
25 |  | A+B |  |  |  | 209758.0684
|  | TOTAL ESTIMATE |  |  | Say Rs. | 209758

## 42
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 42
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR)WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2820.2 | 56404
2 |  | GUY SETS WITH PREFORMED FITTING. | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 60 | 116.46 | 6987.6
WITH FITTING VIZ. U CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 | 01 02 00 0031 | ALL ALU. ALLOY CONDUCTOR 34MM2 SIZE | KM. | 3.09 | 25415 | 78532.35
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 3915.1208
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2.4 | 103.33 | 247.992
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 21.36 | 103.33 | 2207.1288
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 1.5 | 120 | 180
| 26 15 00 0022 | (d) Line spacers for 3 wire line | NO | 40 | 32 | 1280
|  | (Considering 2 spacers / span) |  |  |  | 3915.1208
7 |  | COST OF MATERIALS |  |  |  | 159013.8788
8 |  | ADD:3% CONTINGENCIES |  |  |  | 4770.4164
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 3180.2776
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3180.2776
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 23852.0818
12 |  | A |  |  |  | 193996.9321
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 20 | 878 | 17560
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 3 | 1592 | 4776
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 11 | 209
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES…. |  |  |  | 46619.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6992.865
24 |  | B |  |  |  | 53611.965
25 |  | A+B |  |  |  | 247608.8971
|  | TOTAL ESTIMATE |  |  | Say Rs. | 247609

## 43
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 43
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN - 30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 33 | 2820.2 | 93066.6
2 |  | GUY SETS WITH PREFORMED FITTING. | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 99 | 116.46 | 11529.54
WITH FITTING VIZ. U CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 | 01 02 00 0031 | ALL ALU. ALLOY CONDUCTOR 34MM2 SIZE | KM. | 3.09 | 25415 | 78532.35
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 7485.3332
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 103.33 | 495.984
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 35.24 | 103.33 | 3641.3492
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 1.5 | 120 | 180
| 26 15 00 0022 | (d) Line spacers for 3 wire line | NO | 99 | 32 | 3168
|  | (Considering 3 spacers / span) |  |  |  | 7485.3332
7 |  | COST OF MATERIALS |  |  |  | 208120.4912
8 |  | ADD:3% CONTINGENCIES |  |  |  | 6243.6147
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 4162.4098
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4162.4098
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 31218.0737
12 |  | A |  |  |  | 253906.9993
13 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 33 | 878 | 28974
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 3 | 1592 | 4776
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES…. |  |  |  | 68754.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10313.115
24 |  | B |  |  |  | 79067.215
25 |  | A+B |  |  |  | 332974.2143
|  | TOTAL ESTIMATE |  |  | Say Rs. | 332974

## 44
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 44
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING34 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2820.2 | 56404
2 |  | GUY SETS WITH PREFORMED | NO. | 5 | 1106.138 | 5530.69
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1106.138
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 80 | 116.46 | 9316.8
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 25415 | 104709.8
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 25415 | 104709.8
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 5309.4984
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 103.33 | 206.66
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 28.48 | 103.33 | 2942.8384
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 40 | 48 | 1920
|  | (Considering 2 spacers / span) |  |  |  | 5309.4984
7 |  | COST OF MATERIALS |  |  |  | 187935.1884
8 |  | ADD:3% CONTINGENCIES |  |  |  | 5638.0557
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 3758.7038
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3758.7038
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 28190.2783
12 |  | A |  |  |  | 229280.9298
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 20 | 878 | 17560
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
ITEM NO 22
17 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
18 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 5 | 422 | 2110
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 11 | 209
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5919 | 4439.25
22 |  | LABOUR CHARGES… |  |  |  | 46901.25
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7035.1875
24 |  | B |  |  |  | 53936.4375
25 |  | A+B |  |  |  | 283217.3673
|  | TOTAL ESTIMATE |  |  | Say Rs. | 283217

## 45
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 45
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 9 MTR RSJ POLES 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 33 | 2820.2 | 93066.6
2 |  | GUY SETS WITH PREFORMED | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 132 | 116.46 | 15372.72
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 25415 | 104709.8
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 25415 | 104709.8
6 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 854 | 28182
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 91 | 182
854
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 11698.117
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 18 | 103.33 | 1859.94
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 46.9 | 103.33 | 4846.177
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 48 | 4752
|  | (Considering 3 spacers / span) |  |  |  | 11698.117
8 |  | COST OF MATERIALS |  |  |  | 270535.905
9 |  | ADD:3% CONTINGENCIES |  |  |  | 8116.0772
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 5410.7181
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5410.7181
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 40580.3858
13 |  | A |  |  |  | 330053.8041
14 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
17 |  | LABOUR CHARGES FOR | NO. | 33 | 878 | 28974
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
23 |  | LABOUR CHARGES… |  |  |  | 70346.1
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10551.915
25 |  | B |  |  |  | 80898.015
26 |  | A+B |  |  |  | 410951.8191
|  | TOTAL ESTIMATE |  |  | Say Rs. | 410952

## 46
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 46
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 9 MTR RSJ POLES 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 33 | 15077 | 497541
2 |  | GUY SETS WITH PREFORMED | NO. | 6 | 1106.138 | 6636.828
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1106.138
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 132 | 116.46 | 15372.72
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 25415 | 104709.8
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 25415 | 104709.8
6 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 854 | 28182
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 91 | 182
854
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 10695.816
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 55.2 | 103.33 | 5703.816
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 48 | 4752
|  | (Considering 3 spacers / span) |  |  |  | 10695.816
8 |  | COST OF MATERIALS |  |  |  | 674134.424
9 |  | ADD:3% CONTINGENCIES |  |  |  | 20224.0327
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 13482.6885
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 13482.6885
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 101120.1636
13 |  | A |  |  |  | 822443.9973
14 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
17 |  | LABOUR CHARGES FOR | NO. | 33 | 1395 | 46035
ERECTION OF RSJ POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
22 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5919 | 138149.46
23 |  | LABOUR CHARGES… |  |  |  | 220229.46
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 33034.419
25 |  | B |  |  |  | 253263.879
26 |  | A+B |  |  |  | 1075707.8763
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1075708

## 47
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 47
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 10 MTR PSC POLES 34 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 20 | 5136.54 | 102730.8
2 |  | GUY SETS WITH PREFORMED | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 132 | 116.46 | 15372.72
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 25415 | 104709.8
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 25415 | 104709.8
6 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 20 | 854 | 17080
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 91 | 182
854
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 8823.816
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 55.2 | 103.33 | 5703.816
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 60 | 48 | 2880
|  | (Considering 3 spacers / span) |  |  |  | 8823.816
8 |  | COST OF MATERIALS |  |  |  | 266881.884
9 |  | ADD:3% CONTINGENCIES |  |  |  | 8006.4565
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 5337.6377
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5337.6377
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 40032.2826
13 |  | A |  |  |  | 325595.8985
14 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
17 |  | LABOUR CHARGES FOR | NO. | 20 | 2055 | 41100
ERECTION OF RSJ POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 60 | 11 | 660
22 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
23 |  | LABOUR CHARGES… |  |  |  | 70426.4
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10563.96
25 |  | B |  |  |  | 80990.36
26 |  | A+B |  |  |  | 406586.2585
|  | TOTAL ESTIMATE |  |  | Say Rs. | 406586

## 48
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 48
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2820.2 | 56404
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 5 | 1085.068 | 5425.34
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 80 | 116.46 | 9316.8
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 39982 | 123544.38
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 39982 | 123544.38
6 |  | -DO- BUT 34MM2 AAAC( NEUTRAL WIRE) | KM. | 1.03 | 25415 | 26177.45
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 1.03 | 25415 | 26177.45
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 5309.4984
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 103.33 | 206.66
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 28.48 | 103.33 | 2942.8384
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 40 | 48 | 1920
|  | (Considering 2 spacers / span) |  |  |  | 5309.4984
8 |  | COST OF MATERIALS |  |  |  | 232841.8684
9 |  | ADD:3% CONTINGENCIES |  |  |  | 6985.2561
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4656.8374
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4656.8374
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 34926.2803
13 |  | A |  |  |  | 284067.0794
14 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
17 |  | LABOUR CHARGES FOR | NO. | 20 | 878 | 17560
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 5 | 422 | 2110
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 11 | 209
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5919 | 4439.25
23 |  | LABOUR CHARGES… |  |  |  | 46901.25
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7035.1875
25 |  | B |  |  |  | 53936.4375
26 |  | A+B |  |  |  | 338003.5169
|  | TOTAL ESTIMATE |  |  | Say Rs. | 338004

## 49
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 49
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING PSC POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 33 | 2820.2 | 93066.6
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 132 | 116.46 | 15372.72
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 39982 | 123544.38
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 39982 | 123544.38
6 |  | -DO- BUT 34MM2 AAAC( NEUTRAL WIRE) | KM. | 1.03 | 25415 | 26177.45
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 1.03 | 25415 | 26177.45
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 11129.802
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 55.4 | 103.33 | 5724.482
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 48 | 4752
|  | (Considering 2 spacers / span) |  |  |  | 11129.802
8 |  | COST OF MATERIALS |  |  |  | 286797.62
9 |  | ADD:3% CONTINGENCIES |  |  |  | 8603.9286
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 5735.9524
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5735.9524
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 43019.643
13 |  | A |  |  |  | 349893.0964
14 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
17 |  | LABOUR CHARGES FOR | NO. | 33 | 878 | 28974
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
23 |  | LABOUR CHARGES… |  |  |  | 70346.1
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10551.915
25 |  | B |  |  |  | 80898.015
26 |  | A+B |  |  |  | 430791.1114
|  | TOTAL ESTIMATE |  |  | Say Rs. | 430791

## 50
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 50
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING 9 MTR RSJ POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 33 | 15077 | 497541
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1106.138 | 6636.828
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1106.138
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 132 | 116.46 | 15372.72
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 39982 | 123544.38
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 39982 | 123544.38
6 |  | -DO- BUT 34MM2 AAAC( NEUTRAL WIRE) | KM. | 1.03 | 25415 | 26177.45
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 1.03 | 25415 | 26177.45
7 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 854 | 28182
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 91 | 182
854
8 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 10695.816
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 55.2 | 103.33 | 5703.816
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 48 | 4752
|  | (Considering 3 spacers / span) |  |  |  | 10695.816
9 |  | COST OF MATERIALS |  |  |  | 719146.454
10 |  | ADD:3% CONTINGENCIES |  |  |  | 21574.3936
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 14382.9291
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 14382.9291
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 107871.9681
14 |  | A |  |  |  | 877358.6739
15 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943
DESTINATION
16 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
17 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
18 |  | LABOUR CHARGES FOR | NO. | 33 | 1395 | 46035
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
19 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1592 | 6368
20 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
21 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
22 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
23 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5919 | 138149.46
24 |  | LABOUR CHARGES… |  |  |  | 220229.46
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 33034.419
26
26 |  | B |  |  |  | 253263.879
27 |  | A+B |  |  |  | 1130622.5529
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1130623

## 51
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 51
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (WEASEL)(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2820.2 | 56404
2 |  | GUY SETS WITH PREFORMED FITTINGS | NO. | 5 | 1085.068 | 5425.34
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 110 | 116.46 | 12810.6
WITH FITTING VIZ. V CLAMP AND
|  | GI BOLT | No
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp |  | 1 | 77 | 77
116.46
5 | 01 02 00 0031 | 34MM2 AAAC CONDUCTOR | KM. | 5.15 | 25415 | 130887.25
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 7665.208
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 103.33 | 206.66
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 35.6 | 103.33 | 3678.548
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 60 | 58 | 3480
|  | (Considering 3 spacers / span) |  |  |  | 7665.208
7 |  | COST OF MATERIALS |  |  |  | 219856.798
8 |  | ADD:3% CONTINGENCIES |  |  |  | 6595.7039
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 4397.136
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4397.136
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 32978.5197
12 |  | A |  |  |  | 268225.2936
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 20 | 878 | 17560
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1592 | 7960
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 5 | 422 | 2110
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 60 | 11 | 660
|  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5919 | 4439.25
21 |  | LABOUR CHARGES…. |  |  |  | 48944.25
22 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7341.6375
23 |  | B |  |  |  | 56285.8875
24 |  | A+B |  |  |  | 324511.1811
|  | TOTAL ESTIMATE |  |  | Say Rs. | 324511

## 52
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 52
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (Span-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M 200 KG | NO. | 33 | 2820.2 | 93066.6
2 |  | GUY SETS WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 165 | 116.46 | 19215.9
WITH FITTING VIZ. V CLAMP AND
|  | GI BOLT | No
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp |  | 1 | 77 | 77
116.46
5 | 01 02 00 0031 | 34MM2 AAAC CONDUCTOR | KM. | 5.15 | 25415 | 130887.25
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 11973.142
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 53.4 | 103.33 | 5517.822
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 99 | 58 | 5742
|  | (Considering 3 spacers / span) |  |  |  | 11973.142
7 |  | COST OF MATERIALS |  |  |  | 272649.56
8 |  | ADD:3% CONTINGENCIES |  |  |  | 8179.4868
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 5452.9912
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5452.9912
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 40897.434
12 |  | A |  |  |  | 332632.4632
13 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 33 | 878 | 28974
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1592 | 7960
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
|  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
21 |  | LABOUR CHARGES…. |  |  |  | 71938.1
22 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 10790.715
23 |  | B |  |  |  | 82728.815
24 |  | A+B |  |  |  | 415361.2782
|  | TOTAL ESTIMATE |  |  | Say Rs. | 415361

## 53
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 53
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING 9 MTR RSJ POLE 34 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*100*9 MTR | NO. | 33 | 15077 | 497541
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 165 | 116.46 | 19215.9
WITH H/W & PREFORM FITTINGS.
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AL.ALLOY CONDUCTOR 34 MM2 SIZE. | KM. | 5.15 | 25415 | 130887.25
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 5.15 | 25415 | 130887.25
6 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 0 | 25415 | 0
AND STREET LIGHT
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 0 | 25415 | 0
7 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 854 | 28182
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 91 | 182
854
8 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
|  | BINDING WIRE,LINE SPACER ETC. |  |  |  | 12386.462
WITH PREFORMED FITTINGS
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 61.4 | 103.33 | 6344.462
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 99 | 58 | 5742
|  | (Considering 3 spacers / span) |  |  |  | 12386.462
9 |  | COST OF MATERIALS |  |  |  | 705719.28
10 |  | ADD:3% CONTINGENCIES |  |  |  | 21171.5784
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 14114.3856
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 14114.3856
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 105857.892
14 |  | A |  |  |  | 860977.5216
15 |  | CARTING OF RSJ POLE AT | NO. | 33 | 271 | 8943
DESTINATION
16 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
17 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
18 |  | LABOUR CHARGES FOR | NO. | 33 | 1395 | 46035
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
19 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1592 | 7960
20 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
21 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
22 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
23 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5919 | 138149.46
24 |  | LABOUR CHARGES…. |  |  |  | 221821.46
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 33273.219
26 |  | B |  |  |  | 255094.679
27 |  | A+B |  |  |  | 1116072.2006
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1116072

## 54
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 54
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PHASE 5WIRE FOR AG PURPOSE. VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2820.2 | 56404
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 5 | 1085.068 | 5425.34
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 100 | 116.46 | 11646
WITH H/W & PREFORM FITTINGS.
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 39982 | 123544.38
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 39982 | 123544.38
6 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 2.06 | 25415 | 52354.9
AND STREET LIGHT
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 2.06 | 25415 | 52354.9
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
|  | BINDING WIRE,LINE SPACER ETC. |  |  |  | 7665.208
WITH PREFORMED FITTINGS
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 103.33 | 206.66
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 35.6 | 103.33 | 3678.548
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 60 | 58 | 3480
|  | (Considering 3 spacers / span) |  |  |  | 7665.208
8 |  | COST OF MATERIALS |  |  |  | 263704.228
9 |  | ADD:3% CONTINGENCIES |  |  |  | 7911.1268
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 5274.0846
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5274.0846
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 39555.6342
13 |  | A |  |  |  | 321719.1582
14 |  | CARTING OF PSC POLE AT | NO. | 20 | 271 | 5420
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
17 |  | LABOUR CHARGES FOR | NO. | 20 | 878 | 17560
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1592 | 7960
19 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 5 | 422 | 2110
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 60 | 11 | 660
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5919 | 4439.25
23 |  | LABOUR CHARGES…. |  |  |  | 48944.25
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7341.6375
25 |  | B |  |  |  | 56285.8875
26 |  | A+B |  |  |  | 378005.0457
|  | TOTAL ESTIMATE |  |  | Say Rs. | 378005

## 55
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 55
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING RSJ POLE 55 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*100*9 MTR | NO. | 33 | 15077 | 497541
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 333.22 | 10996.26
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 885.068 | 5310.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
885.068
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 165 | 116.46 | 19215.9
WITH H/W & PREFORM FITTINGS.
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 39982 | 123544.38
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 39982 | 123544.38
6 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 2.06 | 25415 | 52354.9
AND STREET LIGHT
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 2.06 | 25415 | 52354.9
7 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 854 | 28182
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 91 | 182
854
8 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
|  | BINDING WIRE,LINE SPACER ETC. |  |  |  | 12386.462
WITH PREFORMED FITTINGS
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 61.4 | 103.33 | 6344.462
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 99 | 58 | 5742
|  | (Considering 3 spacers / span) |  |  |  | 12386.462
9 |  | COST OF MATERIALS |  |  |  | 749531.31
10 |  | ADD:3% CONTINGENCIES |  |  |  | 22485.9393
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 14990.6262
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 14990.6262
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 112429.6965
14 |  | A |  |  |  | 914428.1982
15 |  | CARTING OF RSJ POLE AT | NO. | 33 | 271 | 8943
DESTINATION
16 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
17 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
18 |  | LABOUR CHARGES FOR | NO. | 33 | 1395 | 46035
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
19 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1592 | 7960
20 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
21 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038
EARTHING WITH SALT AND COAL
22 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 11 | 1089
23 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5919 | 138149.46
24 |  | LABOUR CHARGES…. |  |  |  | 221821.46
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 33273.219
26 |  | B |  |  |  | 255094.679
27 |  | A+B |  |  |  | 1169522.8772
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1169523

## 56
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 56
RE/CITY COST DATA FOR THE YEAR 2022-23
L.T. LINE ADDING OF ONE WIRE IN VERTICAL FORMATION USING55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 2 | 1106.138 | 2212.276
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1106.138
2 |  | LT SHACKLE INSULATOR COMPL. | NO. | 20 | 116.46 | 2329.2
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 24 | 24
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 15.46 | 15.46
| 26 01 00 0040 | (c) U clamp | No | 1 | 77 | 77
116.46
3 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 1.03 | 39982 | 41181.46
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 1.03 | 39982 | 41181.46
4 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 1314.975
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 0.5 | 103.33 | 51.665
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 7 | 103.33 | 723.31
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 0.5 | 120 | 60
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 10 | 48 | 480
|  | (Considering 2 spacers / span) |  |  |  | 1314.975
5 |  | COST OF MATERIALS |  |  |  | 47037.911
6 |  | ADD:3% CONTINGENCIES |  |  |  | 1411.1373
7 |  | ADD:2% STORAGE CHARGES |  |  |  | 940.7582
8 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 940.7582
9 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 7055.6866
10 |  | A |  |  |  | 57386.2514
11 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
12 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 300
13 |  | STRINGING OF CONDUCTOR | KM. | 1 | 1592 | 1592
14 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 2 | 422 | 844
15 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 11 | 209
16 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5919 | 1775.7
17 |  | LABOUR CHARGES… |  |  |  | 5195.7
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 779.355
19 |  | B |  |  |  | 5975.055
20 |  | A+B |  |  |  | 63361.3064
|  | TOTAL ESTIMATE |  |  | Say Rs. | 63361

## 57
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 57
RE/CITY COST DATA FOR THE YEAR 2022-23
SERVICE CONNECTION 3 PHASE 4 WIRE UP TO 5 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 6 | 60 | 360
2 | 16 07 00 0009 | SMC METER BOX 3-Phase | NO. | 1 | 896.21 | 896.21
|  | Three phase SMC meter box | NO. | 1 | 896.21 | 896.21
3 | 16 07 00 0003 | METAL METER BOX 1-Phase | NO. | 0 | 258.6 | 0
|  | Single Phase SMC meter Box | NO. | 0 | 258.6 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 84.19 | 252.57
4 | 04 01 00 0033 | PVC ALUM.4 CX6MM2 UN-ARMOURED CABLE | MTR | 35 | 30.21 | 1057.35
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 412 | 412
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 412 | 412
termination of service (Service Angle)
6 | 16 01 00 0073 | 3 PHASE W.C. L.T. STATIC METER 10/60 AMP. | NO. | 1 | 1868 | 1868
7 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 119.2098
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 95 | 21.736
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 80.65 | 80.65
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw-20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 6 | 0.7 | 4.2
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
119.2098
9 |  | COST OF MATERIALS |  |  |  | 5452.1798
10 |  | ADD:3% CONTINGENCIES |  |  |  | 163.5654
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 109.0436
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 109.0436
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 817.827
14 |  | A |  |  |  | 6651.6594
15 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 391 | 391
SERVICE CONNECTION
16 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 877
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 131.55
18 |  | B |  |  |  | 1008.55
19 |  | A+B |  |  |  | 7660.2094
|  | TOTAL ESTIMATE |  |  | Say Rs. | 7660

## 58
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 58
RE/CITY COST DATA FOR THE YEAR 2022-23
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 5 HP TO 10 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 6 | 60 | 360
2 |  | SMC METER BOX 3-Phase | NO. | 1 | 896.21 | 896.21
| 16 07 00 0009 | Three phase SMC meter box | NO. | 1 | 896.21 | 896.21
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 258.6 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 258.6 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 84.19 | 252.57
4 | 04 01 00 0034 | PVC ALUM.4 CX 10 MM2 UN-ARMOURED CABLE | MTR | 35 | 48.03 | 1681.05
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 412 | 412
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 412 | 412
termination of service (Service Angle)
6 | 16 01 00 0073 | 3 PHASE W.C. L.T. STATIC METER 10/60 AMP. | NO. | 1 | 1868 | 1868
7 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 119.2098
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 95 | 21.736
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 80.65 | 80.65
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 6 | 0.7 | 4.2
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
119.2098
9 |  | COST OF MATERIALS |  |  |  | 6075.8798
10 |  | ADD:3% CONTINGENCIES |  |  |  | 182.2764
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 121.5176
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 121.5176
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 911.382
14 |  | A |  |  |  | 7412.5734
15 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 391 | 391
SERVICE CONNECTION
16 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 877
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 131.55
18 |  | B |  |  |  | 1008.55
19 |  | A+B |  |  |  | 8421.1234
|  | TOTAL ESTIMATE |  |  | Say Rs. | 8421

## 59
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 59
RE/CITY COST DATA FOR THE YEAR 2022-23
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 10 HP TO 20 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 6 | 60 | 360
2 | 16 07 00 0009 | SMC METER BOX 3-Phase | NO. | 1 | 896.21 | 896.21
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 258.6 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 258.6 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 84.19 | 252.57
4 | 04 01 00 0035 | PVC ALUM.4 CX16MM2 UN-ARMOURED CABLE | MTR | 35 | 71.38 | 2498.3
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 412 | 412
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 412 | 412
termination of service (Service Angle)
6 | 16 01 00 0073 | 3 PHASE W.C. L.T. STATIC METER 10/60 AMP. | NO. | 1 | 1868 | 1868
7 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 119.2098
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 95 | 21.736
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 80.65 | 80.65
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 6 | 0.7 | 4.2
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.76 | 9.12
119.2098
9 |  | COST OF MATERIALS |  |  |  | 6893.1298
10 |  | ADD:3% CONTINGENCIES |  |  |  | 206.7939
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 137.8626
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 137.8626
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 1033.9695
14 |  | A |  |  |  | 8409.6184
15 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 391 | 391
SERVICE CONNECTION
16 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 877
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 131.55
18 |  | B |  |  |  | 1008.55
19 |  | A+B |  |  |  | 9418.1684
|  | TOTAL ESTIMATE |  |  | Say Rs. | 9418

## 60
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 60
RE/CITY COST DATA FOR THE YEAR 2022-23
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 20 HP TO 60 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0014 | KIT-KAT FUSE 100 AMPS. | NO. | 6 | 327.69 | 1966.14
2 |  | SMC METER BOX 3-Phase | NO. | 1 | 896.21 | 896.21
| 16 07 00 0009 | Three phase SMC meter box for C.T. Operated meter | NO. | 1 | 896.21 | 896.21
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 258.6 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 258.6 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 84.19 | 252.57
4 | 04 01 00 0003 | 3.5 CORE 50MM2 PVC CABLE. | MTR | 35 | 180.89 | 6331.15
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 412 | 412
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 412 | 412
termination of service (Service Angle)
6 | 16 01 00 0069 | 3 PHASE L.T. STATIC METER 100/5 AMP. C. T. OPERATED. | NO. | 1 | 2240 | 2240
7 | 16 08 00 0046 | RING TYPE L. T. C. T. - 100/5 AMP. | SET | 1 | 1695 | 1695
8 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
9 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 141.3498
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 95 | 21.736
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 80.65 | 80.65
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0028 | (e) Screw - 75x8 ( for 100 Amp Fuse) | NO | 6 | 1.35 | 8.1
| 15 0100 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 13 01 00 0017 | (g) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 36 | 0.76 | 27.36
141.3498
10 |  | COST OF MATERIALS |  |  |  | 14421.2598
11 |  | ADD:3% CONTINGENCIES |  |  |  | 432.6378
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 288.4252
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 288.4252
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2163.189
15 |  | A |  |  |  | 17593.937
16 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 391 | 391
SERVICE CONNECTION
17 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 877
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 131.55
19 |  | B |  |  |  | 1008.55
20 |  | A+B |  |  |  | 18602.487
|  | TOTAL ESTIMATE |  |  | Say Rs. | 18602

## 61
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 61
RE/CITY COST DATA FOR THE YEAR 2022-23
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 60 HP AND ABOVE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0020 | KIT-KAT FUSE 200 AMPS. | NO. | 6 | 772.31 | 4633.86
2 |  | SMC METER BOX 3-Phase | NO. | 1 | 896.21 | 896.21
| 16 07 00 0009 | Three phase SMC meter box for C.T. Operated meter | NO. | 1 | 896.21 | 896.21
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 258.6 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 258.6 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 84.19 | 252.57
4 | 04 01 00 0004 | 3.5 CORE 70MM2 PVC CABLE. | MTR | 35 | 234.5 | 8207.5
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 412 | 412
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 412 | 412
termination of service (Service Angle)
6 | 16 01 00 0070 | 3 PHASE L.T. STATIC METER 200/5 AMP. | NO. | 1 | 2240 | 2240
C. T. OPERATED.
7 | 16 08 00 0047 | RING TYPE L. T. C. T. - 200/5 AMP. | SET | 1 | 888.64 | 888.64
8 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
9 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 201.7698
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 95 | 21.736
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 80.65 | 80.65
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0028 | (e)Bolt type Screw - 1/8 x.2" ( for 200 Amp Fuse) | NO | 6 | 2.3 | 13.8
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 13 01 00 0022 | (g) Tinned Copper Fuse Wire No.10(for 200 Amp. Fuse) | Grams | 108 | 0.76 | 82.08
201.7698
10 |  | COST OF MATERIALS |  |  |  | 18219.3898
11 |  | ADD:3% CONTINGENCIES |  |  |  | 546.5817
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 364.3878
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 364.3878
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2732.9085
15 |  | A |  |  |  | 22227.6556
16 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 391 | 391
SERVICE CONNECTION
17 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 877
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 131.55
19 |  | B |  |  |  | 1008.55
20 |  | A+B |  |  |  | 23236.2056
|  | TOTAL ESTIMATE |  |  | Say Rs. | 23236
4000
19236

## 62
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 62
RE/CITY COST DATA FOR THE YEAR 2022-23
ESTIMATE FOR SINGLE PHASE SERVICE CONNECTION (UP TO 6 KW LOAD )
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 1 | 40 | 40
2 |  | METAL METER BOX BELOW 50 AMPS | NO. | 1 | 258.6 | 258.6
| 16 07 00 0001 | Single Phase SMC meter Box | NO. | 1 | 258.6 | 258.6
3 | 01 03 00 0003 | G.I.WIRE NO.10 (3.15 MM) | KG. | 1.5 | 84.19 | 126.285
4 | 19 01 00 0005 | PVC INSULATED PVC SHEATHED | MTR. | 35 | 9.9 | 346.5
2.5 MM2TWIN CORE CABLE
5 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 1 | 744 | 744
6 | 20 04 00 0001 | REEL INSULATOR | NO. | 60 | 0.65 | 39
7 | 20 05 00 0001 | EGG INSULATOR | NO. | 2 | 1.6 | 3.2
8 | 28 01 00 0015 | PVC PIPE 20 MM DIA (3 MTR PIECE) | NO | 1 | 80.65 | 80.65
9 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
10 |  | COST OF SCREW,BOLTS,BLACK TAPS,
|  | BINDING WIRE ,EARTHING BOLTS ETC. WITH |  |  |  | 6.744
PREFORMED FITTING.
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.0572 | 95 | 5.434
| 15 05 00 0013 | (b) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (c) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.76 | 0.76
6.744
11 |  | COST OF MATERIALS |  |  |  | 2131.819
12 |  | ADD:3% CONTINGENCIES |  |  |  | 63.9546
13 |  | ADD:2% STORAGE CHARGES |  |  |  | 42.6364
14 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 42.6364
15 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 319.7729
16 |  | A |  |  |  | 2600.8192
17 |  | LABOUR CHARGES FOR LAYING OF |  | 1 | 284 | 284
SERVICE CONNECTION
18 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 770
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 115.5
20 |  | B |  |  |  | 885.5
21 |  | A+B |  |  |  | 3486.3192
|  | TOTAL ESTIMATE |  |  | Say Rs. | 3486
725
2761.3192

## 63
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 63
RE/CITY COST DATA FOR THE YEAR 2022-23
ESTIMATE FOR SINGLE PHASE STREET LIGHT CONNECTION
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 1 | 40 | 40
2 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 1 | 744 | 744
3 | 21 05 00 0002 | ICDP SWITCH 32 AMPS./30 AMPS. | NO. | 1 | 140 | 140
4 | 19 01 00 0005 | PVC INSULATED PVC SHEATHED | MTR | 35 | 9.9 | 346.5
2.5 MM2TWIN CORE CABLE
5 | 30 99 00 0002 | CLAMP FOR FIXING PVC PIPE | NO. | 1 | 91 | 91
(M.S.CLAMP FOR ST.LIGHT FIXTURE)
6 | 28 01 00 0015 | PVC PIPE 20 MM DIA 3 MTR | NO | 1 | 80.65 | 80.65
7 |  | METAL METER BOX FOR 1 PHASE | NO. | 1 | 258.6 | 258.6
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 1 | 258.6 | 258.6
8 | 21 07 00 0060 | HOOK CLAMP FOR FIXING (DISTRIBUTION CLAMP) | NO. | 2 | 63 | 126
9 |  | EARTH TERMINAL | NO. | 1 | 486.84 | 486.84
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
10 |  | SUNDRY MATERIAL |  |  |  | 6.744
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.0572 | 95 | 5.434
| 15 05 00 0013 | (b) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (c) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.76 | 0.76
6.744
11 |  | COST OF MATERIALS |  |  |  | 2320.334
12 |  | ADD:3% CONTINGENCIES |  |  |  | 69.61
13 |  | ADD:2% STORAGE CHARGES |  |  |  | 46.4067
14 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 46.4067
15 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 348.0501
16 |  | A |  |  |  | 2830.8075
17 |  | LABOUR CHARGES FOR LAYING OF | No | 1 | 284 | 284
SERVICE CONNECTION
18 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 486 | 486
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 770
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 115.5
20 |  | B |  |  |  | 885.5
21 |  | A+B |  |  |  | 3716.3075
|  | TOTAL ESTIMATE |  |  | Say Rs. | 3716
2182
1534.3075

## 64
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 64
RE/CITY COST DATA FOR THE YEAR 2022-23
ESTIMATE FOR SINGLE PHASE STREET LIGHT FIXTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 1 | 40 | 40
2 | 30 06 00 0007 | STREET LIGHT FIXURE COMPLETE WITH HOLDER | NO. | 1 | 575 | 575
| /0004 | REFLECTOR NIPPLE etc.
3 | 19 01 00 0005 | PVC INSULATED PVC SHETHED | MTR. | 8 | 9.9 | 79.2
2.5 MM2 TWIN CORE CABLE
4 | 30 99 00 0002 | CLAMP FOR FIXING STREET LIGHT FIXURE | NO. | 2 | 91 | 182
INCLUDING BOLT & NUTS.
9 |  | EARTH TERMINAL | NO. |  | 486.84 | 0
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
5 |  | SUNDRY MATERIAL |  |  |  | 1.31
| 15 05 00 0013 | (a) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (b) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.76 | 0.76
1.31
6 |  | COST OF MATERIALS |  |  |  | 877.51
7 |  | ADD:3% CONTINGENCIES |  |  |  | 26.3253
8 |  | ADD:2% STORAGE CHARGES |  |  |  | 17.5502
9 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 17.5502
10 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 131.6265
11 |  | A |  |  |  | 1070.5622
12 |  | LABOUR CHARGES FOR PROVIDING STREET |  |  | ---L.S--- | 250
LIGHT FIXURE
18 |  | ERECTION OF EARTHING COIL/ | NO. |  | 486 | 0
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 250
13 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 37.5
14 |  | B |  |  |  | 287.5 | 41.6
0.5
15 |  | A+B |  |  |  | 1358.0622 | 35.25
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1358 | 514

## 65
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 65
RE/CITY COST DATA FOR THE YEAR 2022-23
LT LINE 1PH 2 WIRE USING ABC OF SIZE 1x 35 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 25 | 2820.2 | 70505
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 333.22 | 8330.5
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 | 405000019 | 1x 35 Sq.mm + 1x35 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 59908.4 | 62903.82
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | 4 | 135 | 540
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
69033.82
|  | COST OF MATERIALS |  |  |  | 154379.728
9 |  | ADD:3% CONTINGENCIES |  |  |  | 4631.3918
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 3087.5946
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3087.5946
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 23156.9592
|  | A |  |  |  | 188343.2682
13 |  | CARTING OF PSC POLE AT | NO. | 25 | 271 | 6775
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 25 | 878 | 21950
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 486 | 12150
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of AB Cable including fittings of All Accessories | KM | 1 | 6471 | 6471
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 2 | 11 | 22
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES… |  |  |  | 56302.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 8445.315
24 |  | B |  |  |  | 64747.415
25 |  | A+B |  |  |  | 253090.6832
|  | TOTAL ESTIMATE |  |  | Say Rs. | 253091

## 66
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 66
RE/CITY COST DATA FOR THE YEAR 2022-23
LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 35 SQ MM + 1x 16 SQ MM + 1x 25 SQ MM ON 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 25 | 2820.2 | 70505
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 333.22 | 8330.5
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 | 405000023 | 3x 35 Sq.mm +1x16 sq.mm. +1x25 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 139440 | 146412
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | 4 | 135 | 540
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
152542
|  | COST OF MATERIALS |  |  |  | 237887.908
9 |  | ADD:3% CONTINGENCIES |  |  |  | 7136.6372
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4757.7582
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4757.7582
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 35683.1862
|  | A |  |  |  | 290223.2478
13 |  | CARTING OF PSC POLE AT | NO. | 25 | 271 | 6775
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 25 | 878 | 21950
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 486 | 12150
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of AB Cable including fittings of All Accessories | KM | 1 | 16178 | 16178
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES… |  |  |  | 66031.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9904.665
24 |  | B |  |  |  | 75935.765
25 |  | A+B |  |  |  | 366159.0128
|  | TOTAL ESTIMATE |  |  | Say Rs. | 366159

## 67
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 67
RE/CITY COST DATA FOR THE YEAR 2022-23
LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 50 SQ MM + 1x 25 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 25 | 2820.2 | 70505
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 333.22 | 8330.5
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 | 405000023 | 3x 50 Sq.mm +1x25 sq.mm. +1x35 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 162113.04 | 170218.692
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | 4 | 135 | 540
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
176348.692
|  | COST OF MATERIALS |  |  |  | 261694.6
9 |  | ADD:3% CONTINGENCIES |  |  |  | 7850.838
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 5233.892
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5233.892
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 39254.19
|  | A |  |  |  | 319267.412
13 |  | CARTING OF PSC POLE AT | NO. | 25 | 271 | 6775
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 25 | 878 | 21950
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 486 | 12150
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of AB Cable including fittings of All Accessories | KM | 1 | 16178 | 16178
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES… |  |  |  | 66031.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9904.665
24 |  | B |  |  |  | 75935.765
25 |  | A+B |  |  |  | 395203.177
|  | TOTAL ESTIMATE |  |  | Say Rs. | 395203

## 68
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 68
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 8 MTR PSC POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 33 | 2820.2 | 93066.6 | 75471
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 333.22 | 10996.26 | 8731.8
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57 | 174.6
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65 | 90
[6 empty] | 333.22 | 264.6
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408 | 5389.44
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260 | 245
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628 | 137
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74 | 71
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44 | 255.24
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21 | 11
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200 | 174
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5 | 5
[6 empty] | 1085.068 | 898.24
4 | 405000023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 578105.58 | 607010.859 | 450783.9
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150 | 3150
7 | 411000073 | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C x 70 sqmm AB Cable for Outdoor Termination application | NO | 6 | 3100 | 18600 | 2430
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900 | 1900
[6 empty] | 631200.859 | 458803.9
|  | COST OF MATERIALS |  |  |  | 741774.127 | 548396.14
9 |  | ADD:3% CONTINGENCIES |  |  |  | 22253.2238 | 16451.8842
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 14835.4825 | 10967.9228
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 14835.4825 | 10967.9228
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 111266.119 | 82259.421
|  | A |  |  |  | 904964.4349 | 669043.2908
13 |  | CARTING OF PSC POLE AT | NO. | 33 | 271 | 8943 | 7260
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475 | 160
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600 | 550
16 |  | LABOUR CHARGES FOR | NO. | 33 | 878 | 28974 | 22275
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532 | 1890
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 486 | 16038 | 11550
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of HT AB Cable including fittings of All Accessories | KM | 1 | 31893 | 31893 | 11000
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 94826.1 | 60039
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 14223.915 | 9005.85
24 |  | B |  |  |  | 109050.015 | 69044.85
25 |  | A+B |  |  |  | 1014014.4499 | 738088.1408
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1014014 | 738088 | 275926

## 69
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 69
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 11 MTR RSJ POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE (116 X 110 X 11 Mtr) | NO. | 25 | 18428 | 460700
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 333.22 | 8330.5
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 | 405000023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 578105.58 | 607010.859
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C x 70 sqmm AB Cable for Outdoor Termination application | NO | 6 | 3100 | 18600
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
631200.859
|  | COST OF MATERIALS |  |  |  | 1106741.767
9 |  | ADD:3% CONTINGENCIES |  |  |  | 33202.253
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 22134.8353
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 22134.8353
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 166011.265
|  | A |  |  |  | 1350224.9557
13 |  | CARTING OF RSJ POLE AT | NO. | 25 | 271 | 6775
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 25 | 1395 | 34875
ERECTION OF RSJ POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 486 | 12150
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of HT AB Cable including fittings of All Accessories | KM | 1 | 31893 | 31893
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES… |  |  |  | 94671.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 14200.665
24 |  | B |  |  |  | 108871.765
25 |  | A+B |  |  |  | 1459096.7207
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1459097

## 70
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 70
RE/CITY COST DATA FOR THE YEAR 2022-23
11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 10 MTR PSC POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 30 | 5136.54 | 154096.2
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 1085.068 | 6510.408
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 88.61 | 354.44
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1085.068
4 | 405000023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 578105.58 | 607010.859
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C x 70 sqmm AB Cable for Outdoor Termination application | NO | 6 | 3100 | 18600
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
631200.859
|  | COST OF MATERIALS |  |  |  | 801804.067
9 |  | ADD:3% CONTINGENCIES |  |  |  | 24054.122
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 16036.0813
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 16036.0813
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 120270.6101
|  | A |  |  |  | 978200.9617
13 |  | CARTING OF 10 mtr PSC POLE AT | NO. | 30 | 450 | 13500
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 475
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 600
16 |  | LABOUR CHARGES FOR | NO. | 30 | 2055 | 61650
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 422 | 2532
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of HT AB Cable including fittings of All Accessories | KM | 1 | 31893 | 31893
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5919 | 5327.1
22 |  | LABOUR CHARGES… |  |  |  | 130601.1
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 19590.165
24 |  | B |  |  |  | 150191.265
25 |  | A+B |  |  |  | 1128392.2267
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1128392

## 71
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 71
RE/CITY COST DATA FOR THE YEAR 2022-23
SINGLE POLE STRUCTURE WITH 11 KV DO FUSE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 1 | 2820.2 | 2820.2
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 635 | 1270
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 1500 MM FOR TOP FABRI. | No | 2 | 635 | 1270
3 |  | CROSS ARM FOR MOUNTING DO Fuse | NO. | 1 | 1016 | 1016
| 36 11 00 0038 | M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 1016 | 1016
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 91 | 364
| 26 01 00 0049 | Side clamp | No | 4 | 91 | 364
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  |  | NO | 1 | 5 | 5
1194.748
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 1 | 333.22 | 333.22
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 1161 | 3483
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 15236.6704 | 16506.47 | 1269.7996
|  | ADD:3% CONTINGENCIES |  |  |  | 457.1001
|  | ADD:2% STORAGE CHARGES |  |  |  | 304.7334
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 304.7334
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2285.5006
11 |  | A |  |  |  | 18588.7378
12 |  | (A) CARTING OF PSC POLE AT | NO. | 1 | 271 | 271
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 905 | 905
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 1 | 486 | 486
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 2 | 422 | 844
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
18 |  | LABOUR CHARGES |  |  |  | 6307.4
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 946.11
20 |  | B |  |  |  | 7253.51
21 |  | A+B |  |  |  | 25842.2478
|  | TOTAL ESTIMATE |  |  | Say Rs. | 25842

## 72
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 72
RE/CITY COST DATA FOR THE YEAR 2022-23
PROVIDING FANCING AROUND DIST. TRANSFORMER CENTRE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) | KG. | 62.48 | 59.6 | 3723.808 | 10.5 mtr | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 Kg/mtr
49.5 mm X 49.5 mm X 4.5 mm
with conversion factor of 5.95 Kg/mtr
2 |  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) | KG | 117.18 | 59.6 | 6983.928
|  | 32 mm X 32 mm X 3.2 mm |  |  |  |  | 43.56 mtr | 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 Kg/mtr
with conversion factor of 2.69 Kg/mtr
3 |  | M.S.Angle 25x25x3mm | KG | 70.72 | 56 | 3960.32
|  | with conversion factor of 1.6 Kg/mtr |  |  |  |  | 44.2 mtr | with conversion factor of 1.6 Kg/mtr
3.2 kg misc
1 kg hanger
4 |  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") | KG | 28.5 | 84.19 | 2399.415
|  | with conversion factor of 3 Kg/Sq. meter | [5 empty] | with conversion factor of 3 Kg/Sq. meter
5 |  | COST OF MATERIALS |  |  |  | 17067.471
6 |  | ADD:3% CONTINGENCIES |  |  |  | 512.0241
7 |  | ADD:2% STORAGE CHARGES |  |  |  | 341.3494
8 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 341.3494
9 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2560.1206
10 |  | A |  |  |  | 20822.3146
11 |  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
12 |  | HINGERS, STOPPERS (Lum Sum) |  | 1 | 770 | 770
13 |  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 693 | 693
14 |  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.2565 | 5919 | 1518.2235
15 |  | LABOUR CHARGES… |  |  |  | 7681.2235
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1152.1835
17 |  | B |  |  |  | 8833.407
18 |  | A+B |  |  |  | 29655.7216
|  | TOTAL ESTIMATE |  |  | Say Rs. | 29656
20822.593
1928.0179

## 73
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 73
RE/CITY COST DATA FOR THE YEAR 2022-23
REPLACEMENT OF SINGLE PHASE SERVICE CONNECTION BY 4.0 MM2 TWIN CORE ARMOURD CABLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 16 07 00 0001 | PVC INSULATED PVC ARMOURD | MTR. | 30 | 38 | 1140
4.o MM2TWIN CORE CABLE
2 | 01 03 00 0003 | G.I.WIRE NO.10 (3.15 MM) | KG. | 1.5 | 170.628 | 255.942
3 | 20 04 00 0001 | REEL INSULATOR | NO. | 30 | 0.65 | 19.5
4 | 20 05 00 0001 | EGG INSULATOR | NO. | 2 | 1.6 | 3.2
5 |  | COST OF MATERIALS |  |  |  | 1418.642
6 |  | ADD:3% CONTINGENCIES |  |  |  | 42.5593
7 |  | ADD:2% STORAGE CHARGES |  |  |  | 28.3728
8 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 28.3728
9 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 212.7963
10 |  | A |  |  |  | 1730.7432
11 |  | LABOUR CHARGES FOR LAYING OF |  | 1 | 187 | 187
SERVICE CONNECTION
12 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 28.05
13 |  | B |  |  |  | 215.05
14 |  | A+B |  |  |  | 1945.7932
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1946
1520

## 74
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 74
RE/CITY COST DATA FOR THE YEAR 2022-23
REPLACEMENT OF SINGLE PHASE MMB BY SMC
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 16 07 00 0001 | Single Phase SMC meter Box | NO. | 1 | 258.6 | 258.6
2 |  | SUNDRY MATERIAL INCLUDING
COST OF SCREW,BOLTS,BLACK TAPS,
|  | BINDING WIRE ,EARTHING BOLTS ETC. WITH |  |  |  | 6.744
PREFORMED FITTING.
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.0572 | 95 | 5.434
| 15 05 00 0013 | (b) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (c) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.76 | 0.76
6.744
3 |  | COST OF MATERIALS |  |  |  | 265.344
4 |  | ADD:3% CONTINGENCIES |  |  |  | 7.9603
5 |  | ADD:2% STORAGE CHARGES |  |  |  | 5.3069
6 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5.3069
7 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 39.8016
8 |  | A |  |  |  | 323.7197
9 |  | Replacement of 1 Ph meter box without meter |  | 1 | 65 | 65
10 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9.75
11 |  | B |  |  |  | 74.75
12 |  | A+B |  |  |  | 398.4697
|  | TOTAL ESTIMATE |  |  | Say Rs. | 398

## 75
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 75
RE/CITY COST DATA FOR THE YEAR 2022-23
SINGLE PHASE METER REPLACEMENT (UP TO 6 KW LOAD )
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 1 | 744 | 744
2 |  | COST OF MATERIALS |  |  |  | 744
3 |  | ADD:3% CONTINGENCIES |  |  |  | 22.32
4 |  | ADD:2% STORAGE CHARGES |  |  |  | 14.88
5 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 14.88
6 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 111.6
7 |  | A |  |  |  | 907.68
8 |  | Replacement of 1 Ph meter only (Rural Area) by another one. |  | 1 | 58 | 58
9 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 8.7
10 |  | B |  |  |  | 66.7
11 |  | A+B |  |  |  | 974.38
12 |  | TOTAL ESTIMATE |  |  | Say Rs. | 974
725
249

## Material
Material Procurement Cost for preparation of COST DATA for the year 2022-23
Sr. No | Item Code | Name | Unit | 2012-13 | 2014-15 | Earlier rates taken in FY 2019-20 | Last purchased end cost with tax rates for FY 2022-23 | Diff | % Rise
1 | 36 04 00 0036 | RSJ POLE 116*110*11MTR | NO. | 10857 | 12878 | 12986 | 18428 | 5442 | 41.91% |  | 16627 | 18428
2 | 26 11 00 0003 | RSJ POLE 116*100*9 MTR | NO. | 8930 | 10536 | 10478 | 15077 | 4599 | 43.89% |  | 0
3 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2010 | 2345 | 2017 | 2820.2 | 803.2 | 39.82% |  | 2016.62
4 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 2990 | 3900 | 3505 | 5136.54 | 1631.54 | 46.55% |  | 3504.6
5 | 36 04 00 0037 | RSJ POLE 150*150*13MTR | NO. |  | 22220 | 17047 | 34312 | 17265 | 101.3% |  | 31054 | 34312
6 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 100MM2 DOG | KM. | 49310 | 50245.51 | 58038 | 73163 | 15125 | 26.06% |  | 75053.9
7 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 WEASEL | KM | 27045 | 27546.48 | 31288 | 39982 | 8694 | 27.79% |  | 41016.8
8 | 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 RABIT | KM | 17050 | 17379.73 | 19989 | 25415 | 5426 | 27.14% |  | 26066.2
9 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 17050 | 17380 | 19989 | 25415 | 5426 | 27.14% |  | 26066.2
10 | 26 09 00 0014 | C TYPE FORMATION | NO | 475 | 540 | 672 | 672 | 0 | 0% |  |  | 672
11 | 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 230 | 264 | 258 | 260 | 2 | 0.7752% |  | 260
12 | 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 125 | 148 | 145 | 170.628 | 25.628 | 17.67% |  | 170.628
13 | 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 65 | 76 | 74 | 74 | 0 | 0% |  | 62
14 | 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 57.39 | 67.15 | 73 | 88.61 | 15.61 | 21.38% |  | 376.59
15 | 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 11 | 11 | 21 | 21 | 0 | 0%
16 | 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 21 | 23.12 | 30 | 42.07 | 12.07 | 40.23% |  | 33.34
17 | 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 144 | 186 | 180 | 200 | 20 | 11.11% | MGVCL
18 | 26 14 0000 17 | (g) Thimble for HT/LT Line | NO | 5 | 5 | 5 | 5 | 0 | 0% |  | 0
19 | 20 02 00 0001 | (a) LT Shackle Insulator | No | 8.5 | 10.64 | 14 | 24 | 10 | 71.43% |  | 15.97 |  | 12.9147
20 | 20 10 00 0002 | (b) LT Shackle Bolt | No | 8.4 | 8.4 | 11 | 15.46 | 4.46 | 40.55% |  | 18.17
21 | 26 01 00 0040 | (c) U clamp | No | 48 | 57 | 56 | 77 | 21 | 37.5% |  | 64
22 | 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 75 | 85 | 70 | 103.33 | 33.33 | 47.61% |  | 61.59 |  | 30.96
23 | 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 75 | 85 | 70 | 103.33 | 33.33 | 47.61% |  | 61 |  | 288.96
24 | 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 75 | 85 | 70 | 103.33 | 33.33 | 47.61% |  | 61
25 | 04 15 00 0019 | (d) P.G. Clamp for Weasle or Rabbit | No | 68 | 76 | 110 | 112.1 | 2.1 | 1.909% | MGVCL | 71.862
26 | 01 01 00 0003 | (c) Alu. Binding wire | KG | 160 | 165 | 120 | 120 | 0 | 0% | MGVCL
27 | 19 05 00 0006 | (d) HT Tape for binding (PVC) | Mtr | 2 | 2.5 | 13 | 13 | 0 | 0%
28 | 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 39 | 43 | 55 | 58 | 3 | 5.455%
29 | 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 29 | 33 | 45 | 48 | 3 | 6.667% | MGVCL | 35
30 | 26 15 00 0022 | (d) Line spacers for 3 wire line | NO | 23 | 27 | 30 | 32 | 2 | 6.667% |  | 25
31 | 26 15 00 0001/2 | (d) Line spacers for 2 wire line | NO | 16 | 20 | 20 | 21 | 1 | 5% |  | 21
32 |  | ANGLE TAPPING FOR 11KV | No |  | 414 | 458 | 635 | 177 | 38.65% |  |  | 635
33 | 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | NO | 56 | 73 | 81 | 113 | 32 | 39.51%
34 | 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | NO | 575 | 723 | 719 | 1016 | 297 | 41.31%
35 | 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | NO | 382 | 466 | 533 | 621 | 88 | 16.51%
36 | 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | NO | 60 | 73 | 185 | 272 | 87 | 47.03%
37 | 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing HG Fuse | NO | 385 | 436 | 428 | 621 | 193 | 45.09%
38 | 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing HG Fuse. | NO | 130 | 150 | 100 | 143 | 43 | 43% |  | 117.6118
39 | 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 195 | 225 | 224 | 321 | 97 | 43.3%
40 | 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 260 | 300 | 298 | 412 | 114 | 38.26% |  | 293.715
41 | 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 1326 | 1538 | 1530 | 2249 | 719 | 46.99% |  | 1714.068
42 | 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 2750 mm | NO | 1115 | 1294 | 1287 | 1850 | 563 | 43.75%
43 | 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 728 | 840 | 834 | 1180 | 346 | 41.49% |  | 1077
44 | 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 728 | 840 | 834 | 1180 | 346 | 41.49%
45 | 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 210 | 243 | 241 | 318 | 77 | 31.95% |  | 235.22
46 | 36 11 00 0031 | Angle Bracing for D.P-65x65x6-750MM | NO. | 195 | 225 | 224 | 592 | 368 | 164.3% |  | 293.71 |  | 592.5
47 | 26 09 00 0029/31 | M.S.Angle 65x65x6mm - 2 Mtr for Guarding Angle cross arm/Guarding channel | No | 528 | 610 | 607 | 857 | 250 | 41.19% |  | 705
48 |  | M.S Angle Tapping-11 KV FEBRI. 65x65x6x1150MM | NO. | 298 | 343 | 341 | 485 | 144 | 42.23%
49 | 21 07 00 0060 | HOOK CLAMP FOR FIXING (DISTRIBUTION CLAMP) | NO. | 50 | 60 | 60 | 63 | 3 | 5% | MGVCL
50 | 26 09 00 0034 | V CROSS ARMS 11KV | NO. | 484 | 559 | 555 | 787 | 232 | 41.8% |  | 600
51 | 27 09 00 0034 | V CROSS ARMS 22KV | NO. | 628 | 725 | 720 | 1021 | 301 | 41.81%
52 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 105 | 123 | 123 | 160 | 37 | 30.08% |  | 203
53 | 06 13 00 0003 | 22 KV A.B. SWITCH 400 AMP. | SET | 16156 | 16156 | 19373 | 19373 | 0 | 0% |  |  | 19373
54 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 5428.5 | 5830 | 7658 | 10185.16 | 2527.16 | 33% |  | 8050 | 10185.16
55 | 13 05 00 0001 | 22 KV.H.G. FUSES. | NO | 2600 | 2600 |  |  | 0 | #DIV/0!
56 | 13 05 00 0001 | 11 KV.H.G. FUSES.(Now DO fuse) | NO | 987 | 987 | 846.06 | 1161 | 314.94 | 37.22% |  | 1161.12
57 | 22 01 00 0004 | 22 KV DIST.TYPE LIGHTENING ARRESTOR | NO | 1260 | 1260 |  |  | 0 | #DIV/0!
58 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO | 356.76 | 356.76 | 309 | 519 | 210 | 67.96% |  | 305.9976
59 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO | 60 | 60 | 60 | 60 | 0 | 0%
60
61 | 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 276.15 | 281.24 | 313 | 313 | 0 | 0% |  | 0 | 313
62 | 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 72.45 | 90.3 | 43 | 80.65 | 37.65 | 87.56% |  | 80.65
63 | 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 54.07 | 61.15 | 73 | 84.19 | 11.19 | 15.33% |  | 69.54
64 | 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 8 | 8.9 | 9 | 9 | 0 | 0%
65 | 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 63 | 104 | 120 | 120 | 0 | 0%
66 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 5103 | 5103.5 | 6900 | 7729 | 829 | 12.01% | MGVCL
67 | 21 04 00 0006 | L.T. DIST. BOX -63 KVA | NO. | 5775 | 6046.95 | 6993 | 9652 | 2659 | 38.02% | MGVCL
68 | 21 04 00 0009 | L.T. DIST. BOX -100 KVA | NO. | 8127 | 8338.68 | 8563 | 12685 | 4122 | 48.14% | MGVCL | 15894
69 | 21 04 00 0009 | L.T. DIST. BOX -200 KVA | NO. | 88044.1 | 88044.1 | 82156 | 82156 | 0 | 0% |  | 99499.96
70 | 21 04 00 0009 | L.T. DIST. BOX -500 KVA | NO. | 167990.24 | 167990.24 | 183748 | 183748 | 0 | 0% |  | 225000.04
71 | 1601000073 | (i) 10-60 A Static Meter | NO | 2249.62 | 2024.34 | 1472 | 1868 | 396 | 26.9% |  | 1646
72 | 1607000009 | (ii) 3-ph SMB | NO | 631.06 | 542.69 | 527 | 642 | 115 | 21.82% |  | 548.11
73 | 1601000070 | (i) 200/5 A Static Meter. | NO | 2540 | 2540 | 1589 | 2240 | 651 | 40.97% |  | 1440
74 | 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 298.73 | 298.73 | 389 | 888.64 | 499.64 | 128.4% |  | 472.59
75 | 1601000069 | (i) 100/5 A Static Meter . | NO | 2539.92 | 2540 | 1589 | 2240 | 651 | 40.97% |  | 1440
76 | 1608000046 | (iv) Ring Type LT CT-100/5 A | SET | 948.36 | 948.36 | 735 | 1695 | 960 | 130.6% |  | 1175
77 | 1608000049 | (iv) Ring Type LT CT-900/5A | SET | 1955 | 1955 | 560 | 560 | 0 | 0% |  |  | 560
78 | 13 02 00 0004 | (c) Fuse element-3 & 5 Amp | NO. | 14 | 15 | 14 | 18 | 4 | 28.57% | MGVCL | 13
79 | 13 02 00 0004 | (c) Fuse element-10 Amp | NO. | 15 | 16 | 14 | 18 | 4 | 28.57% | MGVCL | 13
80 | 13 02 00 0004 | (c) Fuse element-20 Amp | NO. | 15 | 16 | 18 | 18 | 0 | 0% |  | 15
81 | 13 01 00 0006 | (b) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.7 | 0.76 | 0.06 | 8.571% |  | 0.76 | 0.76
82 | 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63/32 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.7 | 0.76 | 0.06 | 8.571% |  | 0.76 | 0.76
83 | 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.7 | 0.76 | 0.06 | 8.571% |  | 0.76 | 0.76
84 | 14 01 00 0017 | (f) Tinned Copper Fuse Wire No.10(for 200 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.7 | 0.76 | 0.06 | 8.571% |  | 0.76 | 0.76
85 | 04 16 00 0004 | (h)Alu.lugs for kit-Kat /Trans. LT 10 SQ.MM Cable | NO. | 2.5 | 2.7 | 1.77 | 1.85 | 0.08 | 4.52% | MGVCL
86 | 26 01 00 0049 | (k)Alu.lugs for kit-Kat/Trans. LT 16 SQ.MM Cable | NO. | 2.5 | 2.7 | 2.7 | 4 | 1.3 | 48.15% | MGVCL
87 | 26 01 00 0049 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 3.25 | 3.2 | 4 | 0.8 | 25% | MGVCL | 2.832
88 | 26 01 00 0049 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 3.5 | 3.75 | 3.54 | 5 | 1.46 | 41.24% | MGVCL | 0
89 | 26 01 00 0049 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 5.1 | 5.5 | 5.5 | 5.5 | 0 | 0% |  | 4.4
90 | 26 01 00 0049 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 7.6 | 8.2 | 8.9 | 8.9 | 0 | 0% |  | 7.12
91 | 26 13 00 0002 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 15.5 | 16.5 | 18.5 | 18.5 | 0 | 0% |  | 14.8
92 | 26 13 00 0002 | (I) Three hole patties | NO. | 20 | 22 | 30 | 43 | 13 | 43.33%
93 | 26 01 00 0049 | (i) Side Clamp | NO. | 57 | 67 | 65 | 91 | 26 | 40%
94 |  | 11KV SDT/SPT 24 A capacity | No | 22939 | 112000 | 112000 | 112000 | 0 | 0%
95 |  | 11KV SDT/SPT 30 A capacity | No | 22939 | 135000 | 135000 | 135000 | 0 | 0%
96 |  | 11KV SDT/PAT 24.7 A capacity | No | 22939 | 190635 | 190635 | 190635 | 0 | 0%
97 |  | 11KV SDT/PAT 54 A capacity | No | 22939 | 278298 | 278298 | 278298 | 0 | 0%
98 |  | Gang operated three pole double throw change over switch | Set | 1 | 7500 | 7611 | 7611 | 0 | 0% |  |  | 7611 |  | 6450 | 7611
99 |  | (e) C.I. Earthing pipe 100 mm dia,13 mm thick | No. | 2 | 5600 | 6136 | 6136 | 0 | 0% |  | 8700 |  |  | 5521 | 6514.78
100 |  | (f) GI Earthing strip (50x6mm) | Kg. | 50 | 30 | 68 | 68 | 0 | 0% |  | 82 |  |  | 5200 | 6136
101 |  | (a) IDMT RELAY | No. | 1 | 4500 | 6515 | 6515 | 0 | 0% |  | 6500 | c&s, stelmac |  | 57.42 | 67.7556
102 |  | (b) HT 11KV C T coil (30/1, 15 VA) | No. | 1 | 10920 | 10920 | 10920 | 0 | 0% |  | 9558
103 |  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 70 | 61 | 61 | 0 | 0% |  | 91.7922
104 |  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 1000 | 527 | 527 | 0 | 0%
105 |  | X'MER 05 KVA 11KV/0.433KV. | No | 22939 | 20772.36 | 37400 | 50000 | 12600 | 33.69% |  | 50000
106 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV. | NO. | 35885.62 | 35033.57 | 32008 | 55700 | 23692 | 74.02% |  | 55700
107 | 44 06 02 0002 | X'MER 16 KVA 11KV/0.433KV. 3 Star | NO. | 46122.03 | 40991.45 | 43400 | 64900 | 21500 | 49.54% |  | 52900
108 | 44 06 02 0002 | X'MER 16 KVA 11KV/0.433KV. 4 Star | NO. | 49450 | 45954.6 | 43400 | 64900 | 21500 | 49.54% |  | 52900
109 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV. 3 Star | NO. | 59111.04 | 48428.07 | 55350 | 77999 | 22649 | 40.92% |  | 64800
110 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV. 4 Star | NO. | 63012.6 | 58281.13 | 55350 | 77999 | 22649 | 40.92% |  | 64800
111 | 44 06 02 0001 | X'MER 63 KVA 11 KV/0.433KV. 4 Star | NO. | 134644.57 | 134644.57 | 95000 | 123800 | 28800 | 30.32% |  | 123800
112 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV. 3 Star | NO. | 100131.7 | 83170.32 | 95000 | 123800 | 28800 | 30.32% |  | 123800
113 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV. 4 Star | NO. | 100131.7 | 100131.7 | 95000 | 123800 | 28800 | 30.32% |  | 123800
114 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. 3 Star | NO. | 133585 | 105881.32 | 124200 | 160800 | 36600 | 29.47% |  | 160800
115 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. 4 Star | NO. | 133585 | 133585 | 124200 | 160800 | 36600 | 29.47% |  | 160800
116 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. 4 Star | NO. | 176211.57 | 176211.57 | 124200 | 160800 | 36600 | 29.47% |  | 160800
117 | 44 06 02 0023 | X'MER 500 KVA 11KV/0.433KV. | NO. | 624750 | 624750 | 849000 | 1103637.48 | 254637.48 | 29.99% |  | 1103637.48
118 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV. 3 Star | NO. | 246787.5 | 222764.93 | 249500 | 427000 | 177500 | 71.14% |  | 299500
119 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV. 4 Star | NO. | 246787.5 | 244067.34 | 249500 | 427000 | 177500 | 71.14% |  | 299500
120 | 614000011 | 11 KV R M U(SF-6) | NO | 360640 | 360640 | 435115 | 482474 | 47359 | 10.88% |  | 482474
121 | 04 05 01 0004 | 3x 35 Sq.mm(P) +1x16 sq.mm.(N) +1x25 sq.mm. bare messenger Aerial Bunched cable | KM | New | 85551.86 | 89796 | 139440 | 49644 | 55.29% |  | 104430 |  | 3x 35 Sq.mm +1x50 sq.mm. +1x25 sq.mm. bare messenger Aerial Bunched cable
122 | New Item | 3x 50 Sq.mm(P) +1x25 sq.mm.(N) +1x35 sq.mm. bare messenger Aerial Bunched cable | KM |  |  | 125513 | 162113.04 | 36600.04 | 29.16%
123 | 405000019 | 1Cx 35 Sq.mm+35mm Aerial Bunched cable | KM | New | 35650.98 | 44527 | 59908.4 | 15381.4 | 34.54% |  | 56899.6
124 | 04 05 01 0023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | New | 352754.48 | 424673 | 578105.58 | 153432.58 | 36.13% |  | 598850
125 | to be deleaded | 11 KV 3x 120 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | New | 530185.21 |  |  | 0 | #DIV/0! |  | 0
126 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | New | 135 | 135 | 135 | 0 | 0% |  |  | 135
127 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | New | 150 | 150 | 150 | 0 | 0%
128 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | New | 135 | 135 | 135 | 0 | 0%
129 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | New | 38.01 | 38 | 38 | 0 | 0%
130 | New Item | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C AB Cable for Outdoor Termination application | NO |  |  | 3100 | 3100 | 0 | 0%
131 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 35.25 | 39.3 | 40 | 40 | 0 | 0% |  |  | 40
132 | 15 05 00 0013 | (a) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 0.48 | 0.55 | 0.55 | 0.55 | 0 | 0%
133 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 50.02 | 50.02 | 60 | 60 | 0 | 0% |  |  | 60
134 | 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 0.6 | 0.7 | 0.7 | 0.7 | 0 | 0%
135 | 13 03 00 0014 | KIT-KAT FUSE 100 AMPS. | NO. | 193.55 | 183.55 | 228 | 327.69 | 99.69 | 43.72% | MGVCL
136 | 15 05 00 0028 | (e) Screw - 75x8 ( for 100 Amp Fuse) | NO | 1.2 | 1.35 | 1.35 | 1.35 | 0 | 0%
137 | 13 03 00 0020 | KIT-KAT FUSE 200 AMPS. | NO. | 538.2 | 505.05 | 582 | 772.31 | 190.31 | 32.7% | MGVCL
138 | 15 05 00 0028 | (e)Bolt type Screw - 1/8 x.2" ( for 200 Amp Fuse) | NO | 2 | 2.3 | 2.3 | 2.3 | 0 | 0%
139 | 30 06 00 0007 | STREET LIGHT FIXURE COMPLETE WITH HOLDER | NO. | 400 | 450 | 575 | 575 | 0 | 0%
140 | 19 01 00 0005 | PVC INSULATED PVC SHETHED 2.5 MM2 TWIN CORE CABLE | MTR. | 5.2 | 5.42 | 6.85 | 9.9 | 3.05 | 44.53% | MGVCL | 8.68
141 | 04 05 00 0009 | 11 KV XLPE CABLE 3 CORE 185 mm2 SIZE. | MTR | 655 | 655 | 1034 | 1039.58 | 5.58 | 0.5397% |  | 1039.58 | 1039.58
142 | 0405000009 | 11KV 240 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 754.3 | 754.3 | 1162 | 1265.22 | 103.22 | 8.883% |  | 1214.22
143 | 04 01 00 0003 | 3.5 CORE PVC INSULATED & SHEATHED 150 MM2 | MTR | 301.7 | 358.26 | 363.44 | 532.98 | 169.54 | 46.65% |  | 532.98
144 | 04 01 00 0004 | 3.5 CORE 70MM2 PVC CABLE. | MTR | 162 | 173.17 | 184.08 | 234.5 | 50.42 | 27.39% |  | 212.87
145 | 04 01 00 0003 | 3.5 CORE 50MM2 PVC CABLE. | MTR | 109.16 | 127.26 | 137.82 | 180.89 | 43.07 | 31.25% |  | 204.376
146 | 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 65.27 | 75.586 | 82.83 | 108.97 | 26.14 | 31.56% |  | 124.05
147 | 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 50.72 | 52.28 | 61.304 | 71.38 | 10.076 | 16.44% |  | 81.03
148 | 04 01 00 0034 | PVC ALUM.4 CX 10 MM2 UN-ARMOURED CABLE | MTR | 35.18 | 35.857 | 41.65 | 48.03 | 6.38 | 15.32% |  | 44.84
149 | 04 01 00 0033 | PVC ALUM.4 CX6MM2 UN-ARMOURED CABLE | MTR | 20.7 | 21.17 | 26.96 | 30.21 | 3.25 | 12.05% |  | 32.59
150 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 834.2 | 779.06 | 465 | 744 | 279 | 60% |  | 488.52
151 | 21 05 00 0002 | ICDP SWITCH 32 AMPS./30 AMPS. | NO. | 70 | 70 | 140 | 140 | 0 | 0% |  |  | 140
152 | 16 07 00 0003 | single phase SMC meter box | NO. | 193.37 | 201.6 | 219 | 258.6 | 39.6 | 18.08% |  | 259.6
153 | 16 07 00 0009 | Three phase SMC meter box for C.T. Operated meter | NO. | 993.6 | 907.2 | 882 | 896.21 | 14.21 | 1.611% |  | 896.21
154 |  | PVC INSULATED PVC ARMOURD 4.0MM2 TWIN CORE CABLE | MTR. | 20 | 61 | 31.32 | 38 | 6.68 | 21.33%
155 | New added | PVC INSULATED PVC ARMOURD 2.5 MM2 TWIN CORE CABLE | MTR. |  |  | 27.263 | 34.15 | 6.887 | 25.26% |  | 38.68
156 | 15 05 00 0044 | (a) Jasati Khila | KG | 70 | 80 | 70 | 95 | 25 | 35.71% |  | 99.12
157 | 01 03 00 0003 | G.I.WIRE NO.10 (3.15 MM) | KG. | 54.07 | 61.15 | 70 | 84.19 | 14.19 | 20.27% |  | 66.08
158 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 54.07 | 61.15 | 73 | 84.19 | 11.19 | 15.33% |  | 66.08
159 | 20 04 00 0001 | REEL INSULATOR | NO. | 0.5 | 0.6 | 0.55 | 0.65 | 0.1 | 18.18% | MGVCL | 0.5664
160 | 20 05 00 0001 | EGG INSULATOR | NO. | 1.75 | 2 | 1.6 | 1.6 | 0 | 0% |  | 1.239
161 | 19 05 00 0002 | (c) LT Tape | Mtr | 1.5 | 1.75 | 1.4769 | 1.4769 | 0 | 0% |  | 6.5
162 | 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 258.59 | 223.46 | 164 | 135 | -29 | -17.68% |  | 135
163 | 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 134.6 | 143.7 | 128 | 281.73 | 153.73 | 120.1% |  | 281.73
164 | 26 01 00 0069 | Guy clamp for two way strain clamp (Stay Pair) | No | 144 | 186 | 180 | 200 | 20 | 11.11% | MGVCL |  | 200
165 | 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 157.7 | 165.28 |  |  | 0 | #DIV/0!
166 | 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 140 | 171.96 |  |  | 0 | #DIV/0!
167 | 20 01 00 0006 | (a)11 KV Pin Insulator (composite) | NO. | 40.74 | 46.49 | 219 | 199.24 | -19.76 | -9.023% |  | 199.24
168 | 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 47.88 | 61.66 |  |  | 0 | #DIV/0!
169 | 04 09 00 0025 | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 200 | 225 | 175 | 331 | 156 | 89.14% |  | 334.70 | 331
170 | 04 19 00 0010 | Doble Compressed 25 mm2 Cable Gland | No. | 130 | 140 | 135 | 135 | 0 | 0%
171 | 16 08 00 0010 | Test Terminal Box | No. | 800 | 875 | 875 | 875 | 0 | 0%
172 | 1607000007 | 3 PH HT Connection SMC Box | No. |  |  | 2714 | 3014.1 | 300.1 | 11.06% | to be add in ht items
173 | 401000040 | 2C 4MM2 PVC CABLE | MTR |  |  | 9.35 | 11 | 1.65 | 17.65% |  | 11.35
401000041

## Labour Rate (hidden)
APPROVED LABOUR RATES FOR WORKS FOR THE YEAR 2022-23
Sr. No | Name | Unit | 2012-13 | 2015-16 | 2019-20 | Approved rate 2022-23 | Diff of FY19-20 | % Rise
1 | SURVEY,TREE CUTTING &COMPENSATION | ----LS---- | 115 | 160 | 400 | 475 | 75 | 18.75% | 400 | 475
2 | CARTING OF LINE MATERIALS TO SITE FOR AB SWITCH/ MISC | ----LS---- | 160 | 220 | 230 | 250 | 20 | 8.696% | 230 | 250
3 | CARTING OF LINE MATERIALS TO SITE FOR TC/LINE | ---LS--- | 390 | 550 | 575 | 600 | 25 | 4.348% | 575 | 600
4 | STRINGING OF CONDUCTOR | KM. | 885 | 1240 | 1373 | 1592 | 219 | 15.95% | 1373 | 1592
5 | STRINGING OF DOG CONDUCTOR. | KM. | 1950 | 2730 | 3162 | 3668 | 506 | 16% | 3162 | 3668
6 | ERECTION OF GUY SET COMPLETE | NO. | 225 | 315 | 364 | 422 | 58 | 15.93% | 364 | 422
7 | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 6 | 8.5 | 9 | 11 | 2 | 22.22% | 9 | 11
8 | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 4200 | 5900 | 5900 | 5919 | 19 | 0.322% | 5900 | 5919
9 | LABOUR CHARGES FOR ERECTION OF T/C.INCL. | NO. | [7 empty] | 0
| PAINTINGING OF STRUCTURE MATERIAL AND | [8 empty] | 0
| PROVIDING LIGHTENING ARRESTOR,HG FUSES, | [8 empty] | 0
| DIST.BOX ETC. ON Single Pole Stucture |  | 2030 | 2860 | 2949 | 3244 | 295 | 10% | 2949 | 3244
10 | LABOUR CHARGES FOR ERECTION OF T/C.INCL. | NO. | [7 empty] | 0
| PAINTINGING OF STRUCTURE MATERIAL AND | [8 empty] | 0
| PROVIDING LIGHTENING ARRESTOR,HG FUSES, | [8 empty] | 0
| DIST.BOX ETC. on duble Pole Structure (8* mtr) |  | 3815 | 5360 | 5900 | 6814 | 914 | 15.49% | 5900 | 6814 |  | DIST.BOX ETC. on duble Pole Structure (10* mtr)
11 | LABOUR CHARGES FOR ERECTION OF T/C.INCL. | NO. | [7 empty] | 0
| PAINTINGING OF STRUCTURE MATERIAL AND | [8 empty] | 0
| PROVIDING LIGHTENING ARRESTOR,HG FUSES, | [8 empty] | 0
| DIST.BOX ETC. on Plinth / RSJ Pole |  | 5285 | 6160 | 6899 | 7589 | 690 | 10% | 6899 | 7589
12 | ERECTION OF EARTHING COIL | NO. | 250 | 350 | 419 | 486 | 67 | 15.99% | 419 | 486
| PLATE TYPE WITH SALT &COAL (10 Kg+10 Kg) | [8 empty] | 0
13 | CARTING OF POLE AT WORK SITE | NO. | 160 | 220 | 246 | 271 | 25 | 10.16% | 246 | 271
14 | CARTING OF POLE AT DEST. 10 Mtr | NO. | 225 | 320 | 400 | 450 | 50 | 12.5% | 400 | 450
13 | CARTING OF RSJ POLE AT DESTINATION | NO. | 160 | 220 | 246 | 271 | 25 | 10.16% | 246 | 271
14 | LABOUR CHARGES FOR LAYING OF | No | 230 | 325 | 355 | 391 | 36 | 10.14% | 355 | 391
| 3 PHASE SERVICE CONNECTION | [8 empty] | 0
15 | LABOUR CHARGES FOR | NO. | 480 | 675 | 757 | 878 | 121 | 15.98% | 757 | 878
| ERECTION OF PSC POLE INCLUDING | [8 empty] | 0
| DIGGING OF PITS, FIXING OF POLE | [8 empty] | 0
| FIXTURE etc. AND PAINTING OF | [8 empty] | 0
| STEEL FIXTURE. | [8 empty] | 0
16 | LABOUR CHARGES FOR ERECTION | NO. | 800 | 1120 | 1268 | 1395 | 127 | 10.02% | 1268 | 1395
| OF RSJ POLE INCLUDING DIGGING. | [8 empty] | 0
| OF PITS,FIXING OF POLES FIXTURE, | [8 empty] | 0
| INSULATOR & PAINTING STEEL POLE | [8 empty] | 0
17 | LABOUR CHARGES FOR ERECTION 10 Mtr | NO. | 1295 | 1815 | 1815 | 2055 | 240 | 13.22% | 1815 | 2055
| OF PSC POLE INCLUDING DIGGING. | [8 empty] | 0
| OF PITS,FIXING OF POLES FIXTURE, | [8 empty] | 0
| INSULATOR & PAINTING STEEL POLE | [8 empty] | 0
18 | INSTALLATION OF ENERGY METER,MM BOX ETC. | ---LS--- | 395 | 550 | 550 | 550 | 0 | 0% | 550 | 550
| ON T/C | [8 empty] | 0
19 | LABOUR CHARGES FOR PROVIDING STREET | ---L.S--- | 150 | 210 | 227 | 250 | 23 | 10.13% | 227 | 250
| LIGHT FIXURE | [8 empty] | 0
20 | PLINTH (3.34*3.34*1.5MTR) FOR MOUNTING X-MER | ---LS--- | 75000 | 105600 | 65715.44 | 65715.44 | 0 | 0% | 65715.44 | 65715.44 | Rate of CMT 3928/-cmt |  | MEHSANA SOR GIVEN BY CIVIL SECTION | 16.73
21 | LABOUR CHARGES FOR ERECTION OF D.O on Single Pole | SET | [7 empty] | 0 |  |  |  | 16.7334
| STRUCTURE ON PSC POLE,HG FUSE |  | 1285 | 905 | 905 | 905 | 0 | 0% | 905 | 905
21 | LABOUR CHARGES FOR ERECTION OF D.P. | SET | [7 empty] | 0 |  |  |  | 46920.4536
| STRUCTURE ON PSC POLE,HG FUSE |  | 1285 | 1810 | 2067 | 2274 | 207 | 10.01% | 2067 | 2274
22 | LABOUR CHARGES FOR ERECTION OF D.P. | SET | [7 empty] | 0
| STRUCTURE ON RSJ POLE WITH | [8 empty] | 0
| AB SWITCH/HG FUSE |  | 1660 | 2335 | 2485 | 2734 | 249 | 10.02% | 2485 | 2734
23 | LABOUR CHARGES FOR ERECTION OF D.P. | SET | [7 empty] | 0
| STRUCTURE ON PSC POLE 10 mtr ,HG FUSE |  | 2865 | 4030 | 4030 | 4433 | 403 | 10% | 4030 | 4433
24 | LABOUR CHARGES FOR COMPLETE | ----LS---- | 380000 | 534000 | 350000 | 350000 | 0 | 0% | 350000 | 350000
| WORK OF UNDERGROUND RIVER CROSSING | [8 empty] | 0
25 | LABOUR CHARGES FOR FIXING (Tapping) | NO. | [7 empty] | 0
| OF CROSS ARMS, BRACING ON LOCATION |  | 135 | 278 | 313 | 363 | 50 | 15.97% | 313 | 363
26 | PROVIDE GUARDING. | MTR | 42 | 58 | 58 | 58 | 0 | 0% | 58 | 58
| COMPLETE WITH PAINTING. | [8 empty] | 0
| LABOUR CHARGES | [8 empty] | 0
27 | LABOUR CHARGES FOR PROVIDING FANCING | ---LS--- | 3350 | 4700 | 4700 | 4700 | 0 | 0% | 4700 | 4700
| AROUND DIST. TRANSFORMER CENTER | [8 empty] | 0
28 | HINGERS, STOPPERS (Lump Sump) | ---LS--- | 550 | 770 | 770 | 770 | 0 | 0% | 770 | 770
29 | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR | ---LS--- | 450 | 630 | 630 | 693 | 63 | 10% | 630 | 693
30 | Labour charge for laying U/G XLPE cable including digging of pit (4 Ft.) and laying of cable with providing Cable Trench with bricks & send providing of cable indicator | MTR. | 220 | 305 | 335 | 335 | 0 | 0% | 271 | 335
31 | LABOUR CHARGES FOR COMPLETE | ----LS---- | [7 empty] | 0
| WORK OF Railway CROSSING |  | 435000 | 612000 | 350000 | 350000 | 0 | 0% | 350000 | 350000
32 | Stringing of of three phase(HT) AB Cable including fittings of All Accessories | KM | New | 11000 | 28994 | 31893 | 2899 | 9.999% | 28994 | 31893
| Stringing of of three phase 4 wisre (LT 3P4W) AB Cable including fittings of All Accessories |  |  |  | 14707 | 16178 | 1471 | 10% | 14707 |  | New Item
33 | Stringing of of single phase AB Cable(LT 1P2W) including fittings of All Accessories | KM | New | 4400 | 5883 | 6471 | 588 | 9.995% | 5883 | 6471
33 | Crimping Of Insulated Mid Span Joint For ABC | NO | New | 11 | 11 | 11 | 0 | 0% | 11 | 11
34 | ERECTION OF EARTHING CHAMBER | NO |  | 2000 | 2000 | 2300 | 300 | 15% | 2000 | 2300
| EXCAVATION OF EART PIT SALT, CHARCOAL & BENTONITE | [8 empty] | 0
35 | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR |  | 30 | 30 | 30 | 0 | 0% | 30 | 30
| DP STRUCTURE WITH XMER ON 10 MTR PSC POLE |  |  |  | 6900 | 6900 | 0 | 0% | 6900 | 6900
36 | PROVIDING SINGLE PHASE SERVICE CONNECTION |  |  |  | 258 | 284 |  |  | 258 | 284
37 | Replacement of 1 Ph old service line by new PVC/Armored service line |  |  |  | 170 | 187 |  |  | 170 | 187
| Replacement of 1 Ph meter box without meter |  |  |  | 50 | 65 |  |  | 50 | 65
| Replacement of 1 Ph meter only (Rural Area) by another one. |  |  |  | 45 | 58 |  |  | 45 | 58
| ERECTION OF DOUBLE POLE STRUCTURE OF 10 METERS 200 KG PSC POLES |  |  |  | 3604 | 4433 |  |  | 3604 | 4433
| Providing & Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 160 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. |  |  |  | 1440 | 1440 |  |  | 1440 | 1440
| Providing and Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 110 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. |  |  |  | 1165 | 1165 |  |  | 1165 | 1165

## Annexure-F
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM WISE COST DATA FOR H.T.POWER SUPPLY FOR FY 2022-23
ANNEXURE-F
SR NO. | ITEM CODE | ITEM NO. | PARTICULARS | PARTICULARS | UNIT | RATE OF 2014-15 | RATE OF 2015-16 | RATE OF 2019-20 | RATE (In Rs.) 22-23 | % Diff.
1 | 2 | 3 |  | 4 | 5 |  |  |  | 6
1 | 9603000051 | ITEM 1 | 0611000033 | 11KV INDOOR FEEDER BREAKER PANEL (VCB) COMPLETE IN ALL RESPECT AT S/S END | No. | 237063 | 297000 | 451052 | 451052 | 0
2 | 9603000016 | ITEM 2 |  | 11KV DP STRUCTURE AT S/S END FOR O/H LINE AND U/G CABLE USING 11 MTR RSJ POLES | No. | 78167.1172 | 75548.932 | 82854.4768 | 106957.3086 | 29.0906
3 | 9603000046 | ITEM 3 | 0405000009 | 11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH | Mtr. | 1121.1 | 1205.97 | 1573.13 | 1653.5376 | 5.1113
4 | 9603000047 | ITEM 4 | 0405000010 | 11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH | Mtr. | 1242.246 | 1401.17 | 1729.29 | 1928.8184 | 11.5382
5 | NEW | ITEM 5 |  | 11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD | Mtr. |  |  | 2601.23 | 2608.0376 | 0.26171
6 |  | ITEM 6 |  | 11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD | Mtr. |  |  | 3073.64 | 3199.5684 | 4.097
7 | 9603000001 | ITEM 7 |  | 11KV TAPPING FROM EXISTING POLE | No. | 6191.6175 | 5881.0782 | 6498.18 | 8611.5808 | 32.523
8 | 9603000002 | ITEM 8 |  | 11KV D. P. STRUCTURE WITH A. B. SWITCH USING 8 MTR PSC POLES. | No. | 36033.4172 | 36743.722 | 38928.5868 | 48715.6206 | 25.141
9 | 9603000057 | ITEM 9 |  | 11KV D. P. STRUCTURE WITH H.G. FUSE USING 8 MTR PSC POLES (WITHOUT AB SWITCH) | No. | 31884.1972 | 31223.222 | 31950.4064 | 39654.5342 | 24.1128
10 | 9603000003 | ITEM 10 |  | 11KV D. P. STRUCTURE A. B. SWITCH USING 9 MTR RSJ POLES. | No. | 66303.8372 | 64822.692 | 70233.3268 | 89740.7686 | 27.7752
11 | 9603000060 | ITEM 11 |  | 11KV D. P. STRUCTURE WITH H.G. FUSE USING 9 MTR RSJ POLES. | No. | 52422.2372 | 48772.772 | 53075.9464 | 70090.1262 | 32.0563
12 | 9603000004 | ITEM 12 |  | 11KV D. P. STRUCTURE A. B. SWITCH USING 11 MTR RSJ POLES. | No. | 72018.3172 | 70015.012 | 76749.5968 | 98319.7086 | 28.1045
13 | 9603000059 | ITEM 13 |  | 11KV D. P. STRUCTURE H.G.FUSE USING 11 MTR RSJ POLES. | No. | 58136.7172 | 53965.092 | 59195.4664 | 78266.5662 | 32.2172
14 | 9603000005 | ITEM 14 |  | 11KV LINE WITH 55MM2 AAA CONDUCTOR USING 8 MTR/ 200 KG PSC POLES. WPZ - 100 KG/M2(SPAN 50 MTRS.) | KM | 243382.4825 | 251401.406 | 264765.2664 | 333879.3014 | 26.1039
15 | 9603000006 | ITEM 15 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-33 MTR) | KM | 846156.9185 | 813861.008 | 903056.7624 | 1161476.0432 | 28.6161
16 | 9603000061 | ITEM 16 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-50 MTR) | KM | 610866.1785 | 591576.812 | 653787.6624 | 839402.7952 | 28.3907
17 | 9603000062 | ITEM 17 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE- 9 MTR (SPAN-50 MTR) | KM | 553721.3785 | 539653.612 | 592592.4624 | 757638.3952 | 27.8515
18 | 9603000050 | ITEM 18 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON PSC POLE(SPAN-33 MTR) | KM | 317208.8437 | 324355.211 | 341478.7084 | 429647.4366 | 25.8197
19 | 9603000008 | ITEM 19 |  | 11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (33 MTR. SPAN) | KM | 974192.3126 | 954040.502 | 996865.6824 | 1284364.625 | 28.8403
20 | 9603000009 | ITEM 20 |  | 11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (50 MTR SPAN) | KM | 723279.8386 | 716590.364 | 747918.6624 | 959815.8702 | 28.3316
21 | 9603000010 | ITEM 21 |  | 11KV RAILWAY CROSSING BY 185 MM2 U/G XLPE CABLE. ( DOUBLE CKT 115 MTR LENGTH) | NO. | 653229.8646 | 663160.882 | 775184.03 | 802657.6406 | 3.5441
19 | 9603000011 | ITEM 22 |  | GUARDING FOR H.T./ L.T.LINES AND P&T LINES | Mtr. | 7392.228 | 7517.8652 | 8237.94 | 9284.6589 | 12.7061
20 | 9603000012 | ITEM 23 |  | 11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 8 MTR PSC POLES | No. | 61529.9736 | 61659.3114 | 65320.6112 | 80322.7067 | 22.9669
21 | 9603000013 | ITEM 24 |  | 11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 11 MTR RSJ POLES | No. | 87292.3336 | 84000.0714 | 92457.9012 | 117991.5887 | 27.6166
22 | 9603000063 | ITEM 25 |  | 11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 9 MTR RSJ POLES | No. | 79240.0896 | 76465.3514 | 84036.2412 | 107432.2325 | 27.8404
23 | 9603000049 | ITEM 26 |  | RIVER CROSSING USING 10 MTR PSC POLES FOR 11KV | No. | 72963.5788 | 70482.5572 | 72958.142 | 92840.8263 | 27.2522
24 | 9603000015 | ITEM 27 |  | RIVER CROSSING USING 11 MTR RSJ POLES FOR 11KV | No. | 129970.8988 | 123089.8572 | 134274.082 | 171362.2431 | 27.6212
SUB TOTAL OF COLUMN NO.6 ( I.E. ITEM 1 TO ITEM 27 )
26 |  | ITEM 28 |  | SERVICE CONNECTION CHARGES
27 |  |  |  | 1) Up to 500 KVA | No. | 9000 | 9000 | 9000 | 9000 | 0
28 |  |  |  | 2) 500 KVA to 1000 KVA | No. | 9000 Plus 1400 per 100 KVA above 500KVA | 9000 Plus 1400 per 100 KVA above 500KVA | 9000 Plus 1400 per 100 KVA above 500KVA | 9000 Plus 1400 per 100 KVA above 500KVA | 0
29 |  |  |  | 3) Above 1000 KVA | No. | 16000 Plus 1700 per 100 KVA above 1000KVA | 16000 Plus 1700 per 100 KVA above 1000KVA | 16000 Plus 1700 per 100 KVA above 1000KVA | 16000 Plus 1700 per 100 KVA above 1000KVA | 0
TOTAL COST TO BE BORNE BY APPLICANT (SUBTOTAL FROM ITEM 21 TO ITEM 27 AND ITEM 28)
30 | 9603000017 | ITEM 29 | 1605000007 | 1)COST OF TVM - 5 Amp Sec | No. | 8312.9 | 8312.9 | 5599 | 11800 | 110.7519
31 | 9603000018 | ITEM 30 | 1605000008 | 2)COST OF TVM - 1 Amp Sec | No. | 19275.83 | 19275.83 | 26054.06 | 36850 | 41.4367
32 | 9603000019 | ITEM 31 | 4456000030 | 1)COST OF 11 KV CTPT SET 10/5 A | No. | 41872.64 | 42113 | 25783 | 36142.28 | 40.1787
33 | 9603000020 | ITEM 32 | 4456000031 | 2)COST OF 11 KV CTPT SET 15/5 A | No. | 37578.8 | 37796 | 24249 | 34332.11 | 41.5815
34 | 9603000021 | ITEM 33 | 4456000034 | 3)COST OF 11 KV CTPT SET 20/5 A | No. | 37497.34 | 36438 | 23280 | 32926.07 | 41.435
35 | 9603000023 | ITEM 34 | 4456000038 | 5)COST OF 11 KV CTPT SET 30/5 A | No. | 32496.98 | 32153 | 23280 | 33181.05 | 42.5303
36 | 9603000024 | ITEM 35 | 4456000040 | 6)COST OF 11 KV CTPT SET 40/5 A | No. | 32496.98 | 32153 | 23280 | 33053.56 | 41.9826
37 | 9603000025 | ITEM 36 | 4456000042 | 7)COST OF 11 KV CTPT SET 50/5 A | No. | 32750 | 32153 | 23280 | 32862.32 | 41.1612
38 | 9603000026 | ITEM 37 | 4456000043 | 8)COST OF 11 KV CTPT SET 75/5 A | No. | 32297.88 | 32153 | 23280 | 37799.71 | 62.3699
39 | 9603000027 | ITEM 38 | 4456000048 | 9)COST OF 11 KV CTPT SET 100/5A | No. | 32097.88 | 32153 | 24367 | 37838.88 | 55.2874
40 | 9603000064 | ITEM 39 | 4456000039 | 10)COST OF 11 KV CTPT SET 150/5 A | No. | 32097.88 | 32153 | 24367 | 38780.7 | 59.1525
41 | 9603000028 | ITEM 40 | 4456000045 | 11)COST OF 11 KV CTPT SET 200/5 A | No. | 43497.36 | 39218 | 24367 | 40101.12 | 64.5714
42 | 9603000056 | ITEM 41 | 4456000046 | 12)COST OF 11 KV CTPT SET 250/5 A | No. | 43497.36 | 39218 | 24367 | 38611.58 | 58.4585

## H2
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 2
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV DP STRUCTURE AT S/S END FOR O/H LINE AND U/G CABLE USING 11 MTR RSJ POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11MTR | NO. | 2 | 18428 | 36856
2 |  | TOP CROSS ARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS BRACING ANGLE SET (4 ANGLES/SET) | SET | 2 | 4720 | 9440
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV | No | 4 | 1180 | 4720
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 91 | 1456
| 26 01 00 0049 | Side clamp | No | 16 | 91 | 1456
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | Thimbal for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 | [5 empty] | 70573.3464
|  | COST OF MATERIALS |  |  |  | 70573.3464
|  | ADD:3% CONTINGENCIES |  |  |  | 2117.2004
|  | ADD:2% STORAGE CHARGES |  |  |  | 1411.4669
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1411.4669
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 10586.002
|  | Total ….A |  |  |  | 86099.4826
11 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 271 | 542
DESTINATION
12 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
13 |  | LABOUR CHARGES FOR ERECTION OF D.P. |  |  |  |  | MM | 700 | 700 | 1400
|  | STRUCTURE ON RSJ POLE WITH | [5 empty] | L | B | H
|  | AB SWITCH/HG FUSE | SET | 1 | 2734 | 2734 |  | 0.7 | 0.7 | 1.4
[7 empty] | CMT | 0.686
14 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
15 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
16 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
17 |  | LABOUR CHARGES |  |  |  | 18137.24
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2720.586
19 |  | B |  |  |  | 20857.826
20 |  | Total ( A+B ) |  |  |  | 106957.3086
|  | Total Estimate |  |  | Say Rs. | 106957.3086

## H3
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 3
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 185 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1039.58 | 1039.58
|  | ADD:3% CONTINGENCIES |  |  |  | 31.1874
|  | ADD:2% STORAGE CHARGES |  |  |  | 20.7916
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 20.7916
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 155.937
|  | Total ….A |  |  |  | 1268.2876
B
2 | 9909000003 | Laying (including installation, testing and commissioning) of various size of Single circuit 11 KV XLPE insulated Aluminium armoured Cable in ground 1200 mm deep and 300 mm wide trench, providing sand cushioning below (75 mm thick layer of sand) and above (75 mm thick layer of sand) of the cable and covering it with RCC half round hume pipe (150 mm inner diameter with thickness of 30 mm and One meter in length) before refilling pre-bonding tap/warning tap should provide below 700 mm from the ground level and back filling the same to make ground level as per original. As per specification and drawing of UGVCL. ( RCC half round pipe should be provide throughout on cable without gap). Only Cable will be supplied by UGVCL. | Mtr. | 1 | 335 | 335 | new code generated
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 50.25
4 |  | Total B |  |  |  | 385.25
5 |  | Total A + B |  |  |  | 1653.5376
|  | TOTAL |  |  | Say Rs. | 1653.5376

## H4
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 4
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 240 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1265.22 | 1265.22
|  | ADD:3% CONTINGENCIES |  |  |  | 37.9566
|  | ADD:2% STORAGE CHARGES |  |  |  | 25.3044
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 25.3044
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 189.783
|  | Total ….A |  |  |  | 1543.5684
B
2 | 9909000003 | Laying (including installation, testing and commissioning) of various size of Single circuit 11 KV XLPE insulated Aluminium armoured Cable in ground 1200 mm deep and 300 mm wide trench, providing sand cushioning below (75 mm thick layer of sand) and above (75 mm thick layer of sand) of the cable and covering it with RCC half round hume pipe (150 mm inner diameter with thickness of 30 mm and One meter in length) before refilling pre-bonding tap/warning tap should provide below 700 mm from the ground level and back filling the same to make ground level as per original. As per specification and drawing of UGVCL. ( RCC half round pipe should be provide throughout on cable without gap). Only Cable will be supplied by UGVCL. | Mtr. | 1 | 335 | 335 | New code generaated
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 50.25
4 |  | Total B |  |  |  | 385.25
5 |  | Total A + B |  |  |  | 1928.8184
|  | TOTAL |  |  | Say Rs. | 1928.8184

## H5.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 5
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 185 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1039.58 | 1039.58
|  | ADD:3% CONTINGENCIES |  |  |  | 31.1874
|  | ADD:2% STORAGE CHARGES |  |  |  | 20.7916
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 20.7916
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 155.937
|  | Total ….A |  |  |  | 1268.2876
B
2 | 9909000003 | Providing and Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 110 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. | Mtr. | 1 | 1165 | 1165 | new code generated
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 174.75
4 |  | Total B |  |  |  | 1339.75
5 |  | Total A + B |  |  |  | 2608.0376
|  | TOTAL |  |  | Say Rs. | 2608.0376

## H6.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 6
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 240 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1265.22 | 1265.22
|  | ADD:3% CONTINGENCIES |  |  |  | 37.9566
|  | ADD:2% STORAGE CHARGES |  |  |  | 25.3044
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 25.3044
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 189.783
|  | Total ….A |  |  |  | 1543.5684
B
2 | 9909000003 | Providing & Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 160 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. | Mtr. | 1 | 1440 | 1440 | New code generaated
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 216
4 |  | Total B |  |  |  | 1656
5 |  | Total A + B |  |  |  | 3199.5684
|  | TOTAL |  |  | Say Rs. | 3199.5684

## H7.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 7
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV TAPPING FROM EXISTING POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | STRAIGHT CROSS ARMS. (1.15 Mtr) | NO. | 2 | 485 | 970
| 36 11 00 0018 | M.S Angle Tapping-11KV FEBRI. 65x65x6x1150MM | NO. | 2 | 485 | 970
2 |  | BRACING FOR SIDE ARM | NO. | 2 | 592 | 1184
| 36 11 00 0031 | Angle Bracing for D.P-65x65x6-750MM | NO. | 2 | 592 | 1184
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 1 | 1194.748 | 1194.748
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 1 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
4 |  | 11KV PIN INSULATORS WITH SPINDLE | SET | 1 | 199.24 | 199.24
| 20 01 00 0006 | (a) 11 KV Pin Insulator | No | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | No | 1 | 0 | 0
199.24
5 |  | 11KV STRAIN INSULATORS WITH H/W | SET | 3 | 416.73 | 1250.19
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
6 |  | M.S. BOLTS OF ASSORTED SIZES &
P.G. CLAMPS OR WITH PREFORMED
|  | FITTINGS. |  |  |  | 501.628
| 15 01 00 0024 | M.S. Bolts & Nuts - 65X16MM | KG | 1.6 | 103.33 | 165.328
| 2601 00 0027/28 | P.G. Clamp for Weasel/Rabbit | Nos | 3 | 112.1 | 336.3
501.628
7 |  | CLAMP FOR BRACING AND CROSS ARMS | PAIR | 1 | 182 | 182
| 26 01 00 0049 | Side clamp | Nos. | 2 | 91 | 182
8 |  | COST OF MATERIALS |  |  |  | 5481.806
9 |  | A |  |  |  | 5481.806
|  | ADD:3% CONTINGENCIES |  |  |  | 164.4542
|  | ADD:2% STORAGE CHARGES |  |  |  | 109.6361
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 109.6361
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 822.2709
|  | Total ….A |  |  |  | 6687.8033
10 |  | LABOUR CHARGES FOR FIXING
|  | OF CROSS ARMS, BRACING ON LOCATION | NO. | 1 | 363 | 363
11 |  | ERECTION OF STAY SETS. | NO. | 1 | 422 | 422
12 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.15 | 5919 | 887.85
13 |  | LABOUR CHARGES |  |  |  | 1672.85
14 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 250.9275
15 |  | B |  |  |  | 1923.7775
16 |  | Sub Total(A+B) |  |  |  | 8611.5808
|  | Total Estimate |  |  | Say Rs. | 8611.5808
Note on F24: R C DESAI(SIR): BASE OLD RATE AS CURRENT RATE IS LOW

## H8.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 8
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D. P. STRUCTURE WITH A. B. SWITCH USING 8 MTR PSC POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2820.2 | 5640.4 |  | Material Code | Material Name | Uom | Qty | Unit Value | Flag | Margin Value | Company % | Consumer %
[7 empty] | 1270 | 3611000016 | MS ANGLE TOP FAB 65X65X6MM 11KV 2750MM | NO | 2 | 635 | PERCENT | 0 | 0 | 100
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360 | 1270 | 3611000038 | MS ANGLE 11KV HG FUSE FABRICATED65X65X6X2750MM | NO | 2 | 635 | PERCENT | 0 | 0 | 100
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360 | 549.648 | 1501000024 | M S BOLTS AND NUTS 65 MM X 16 MM_( 2.5 X 5/8 INCH) | KG | 7.2 | 76.34 | PERCENT | 0 | 0 | 100
[7 empty] | 190.0866 | 1501000031 | M S BOLTS AND NUTS 180 MM X 16 MM_( 7 X 5/8 INCH ) | KG | 2.49 | 76.34 | PERCENT | 0 | 0 | 100
3 |  | CROSS ARM FOR MOUNTING A.B SWITCH. | NO. | 2 | 1180 | 2360 | 28 | 1905000006 | HT ADHESIVE TAPE ROLLS | NO | 20 | 1.4 | PERCENT | 0 | 0 | 100
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360 | 480 | 2601000069 | STAY CLAMP FOR PSC POLES | PR | 4 | 120 | PERCENT | 0 | 0 | 100
[7 empty] | 1863.3 | 2006000001 | 11 KV DISC INSULATOR PLAIN 7000 KG | NO | 6 | 310.55 | PERCENT | 0 | 0 | 100
[7 empty] | 76 | 2003000001 | GUY INSULATOR H .T PORCELAIN | NO | 4 | 19 | PERCENT | 0 | 0 | 100
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16 | 899.82 | 2010000077 | 11 KV DISC HARDWARE | SET | 6 | 149.97 | PERCENT | 0 | 0 | 100
[7 empty] | 720 | 2601000027 | PG CLAMPS FOR WEASEL | NO | 9 | 80 | PERCENT | 0 | 0 | 100
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 91 | 364 | 204 | 2601000049 | C CLAMP FOR PSC POLES | NO | 4 | 51 | PERCENT | 0 | 0 | 100
|  | A B Switch |  |  |  |  | 140 | 2801000015 | PVC RIGID PIPE 20M M | MTR | 2 | 70 | PERCENT | 0 | 0 | 100
| 26 01 00 0049 | Side clamp | No | 4 | 91 | 364 | 40 | 101000003 | ALL ALUM BINDING WIRE 8 SWG 4 MM | KG | 0.5 | 80 | PERCENT | 0 | 0 | 100
[7 empty] | 351.6 | 103000002 | G I WIRE 8 SWG 4MM | KG | 6 | 58.6 | PERCENT | 0 | 0 | 100
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992 | 1140 | 103000012 | G I STAY WIRE 7/10 SWG 7/3.15 MM | KG | 20 | 57 | PERCENT | 0 | 0 | 100
|  | Material required for1 No. Guy set |  |  |  |  | 5071 | 613000003 | 11 KV G.O SWITCH W/O EARTH BLADE 400 AMP | SET | 1 | 5071 | PERCENT | 0 | 0 | 100
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260 | 3460 | 2611000003 | PSC POLES 200 KG 8 METER READY MADE | No | 2 | 1730 | PERCENT | 0 | 0 | 100
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628 | 1224 | 2614000002 | ANCHOR RODS | NO | 4 | 306 | PERCENT | 0 | 0 | 100
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74 | 440 | 2614000009 | TURN BUCKLE MS 16MM | NO | 4 | 110 | PERCENT | 0 | 0 | 100
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05 | 188 | 2614000012 | EYE BOLT WITH NUT | NO | 4 | 47 | PERCENT | 0 | 0 | 100
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07 | 19605.4546
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  |  | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 31185.7464
11 |  | A |  |  |  | 31185.7464
|  | ADD:3% CONTINGENCIES |  |  |  | 935.5724
|  | ADD:2% STORAGE CHARGES |  |  |  | 623.7149
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 623.7149
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 4677.862
|  | Total ….A |  |  |  | 38046.6106
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 271 | 542
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 2274 | 2274
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
18 |  | LABOUR CHARGES |  |  |  | 9277.4
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1391.61
20
21 |  | B |  |  |  | 10669.01
22 |  | Sub Total(A+B) |  |  |  | 48715.6206
|  | Total Estimate |  |  | Say Rs. | 48715.6206

## H9.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 9
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D. P. STRUCTURE WITH H.G. FUSE USING 8 MTR PSC POLES (WITHOUT AB SWITCH)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING HG FUSE | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 91 | 182
FOR HG FUSE.
| 26 01 00 0049 | Side clamp | No | 2 | 91 | 182
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
9 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 1161 | 3483
10 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1787.4144
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 103.33 | 537.316
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601000027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1787.4144
11 |  | COST OF MATERIALS |  |  |  | 23758.6264
12 |  | A |  |  |  | 23758.6264
|  | ADD:3% CONTINGENCIES |  |  |  | 712.7588
|  | ADD:2% STORAGE CHARGES |  |  |  | 475.1725
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 475.1725
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 3563.794
|  | Total ….A |  |  |  | 28985.5242
13 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 271 | 542
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE,HG FUSE | SET | 1 | 2274 | 2274
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
15 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
16 |  | LABOUR CHARGES |  |  |  | 9277.4
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1391.61
18 |  | B |  |  |  | 10669.01
19 |  | Sub Total(A+B) |  |  |  | 39654.5342
|  | Total Estimate |  |  | Say Rs. | 39654.5342

## H10.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 10
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D. P. STRUCTURE A. B. SWITCH USING 9 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 2 | 15077 | 30154
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING HG FUSE/A.B SWITCH. | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 91 | 1456
| 26 01 00 0049 | Side clamp | No | 16 | 91 | 1456
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  |  | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 56791.3464
11 |  | A |  |  |  | 56791.3464
|  | ADD:3% CONTINGENCIES |  |  |  | 1703.7404
|  | ADD:2% STORAGE CHARGES |  |  |  | 1135.8269
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1135.8269
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8518.702
|  | Total ….A |  |  |  | 69285.4426
12 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 271 | 542
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON RSJ POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 2734 | 2734
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
18 |  | LABOUR CHARGES |  |  |  | 17787.24
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2668.086
20
21 |  | B |  |  |  | 20455.326
22 |  | Sub Total(A+B) |  |  |  | 89740.7686
|  | Total Estimate |  |  | Say Rs. | 89740.7686

## H11.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 11
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D. P. STRUCTURE WITH H.G. FUSE USING 9 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 2 | 15077 | 30154
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING HG FUSE | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 91 | 182
FOR HG FUSE.
| 26 01 00 0049 | Side clamp | No | 2 | 91 | 182
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 1161 | 3483
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1787.4144
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 103.33 | 537.316
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1787.4144
10 |  | COST OF MATERIALS |  |  |  | 48272.2264
11 |  | A |  |  |  | 48272.2264
|  | ADD:3% CONTINGENCIES |  |  |  | 1448.1668
|  | ADD:2% STORAGE CHARGES |  |  |  | 965.4445
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 965.4445
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 7240.834
|  | Total ….A |  |  |  | 58892.1162
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 271 | 542
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
13 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE,HG FUSE | SET | 1 | 2734 | 2734
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
14 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
15 |  | LABOUR CHARGES |  |  |  | 9737.4
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1460.61
17 |  | B |  |  |  | 11198.01
18 |  | Sub Total(A+B) |  |  |  | 70090.1262
|  | Total Estimate |  |  | Say Rs. | 70090.1262

## H12.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 12
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D. P. STRUCTURE WITH H.G. FUSE USING 9 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110* 11MTR | NO. | 2 | 18428 | 36856
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING HG FUSE/A.B SWITCH. | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 10185.16 | 10185.16
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 91 | 1456
| 26 01 00 0049 | Side clamp | No | 16 | 91 | 1456
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
|  | Material required for 1 No. earthing |  |  |  | 1194.748
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 2330.3744
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 103.33 | 743.976
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
2330.3744
10 |  | COST OF MATERIALS |  |  |  | 63493.3464
11 |  | A |  |  |  | 63493.3464
|  | ADD:3% CONTINGENCIES |  |  |  | 1904.8004
|  | ADD:2% STORAGE CHARGES |  |  |  | 1269.8669
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1269.8669
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 9524.002
|  | Total ….A |  |  |  | 77461.8826
12 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 271 | 542
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON RSJ POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 2734 | 2734
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
18 |  | LABOUR CHARGES |  |  |  | 18137.24
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2720.586
20 |  | B |  |  |  | 20857.826
21 |  | Sub Total(A+B) |  |  |  | 98319.7086
|  | Total Estimate |  |  | Say Rs. | 98319.7086

## H13.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 13
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D. P. STRUCTURE H.G.FUSE USING 11 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000013 | RSJ POLE 116*110* 11MTR | NO. | 2 | 18428 | 36856
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 1180 | 2360
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 1180 | 2360
3 |  | CROSS ARM FOR MOUNTING HG FUSE | NO. | 2 | 1180 | 2360
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 1180 | 2360
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 91 | 182
FOR HG FUSE.
| 26 01 00 0049 | Side clamp | No | 2 | 91 | 182
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 333.22 | 666.44
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 416.73 | 2500.38
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 135 | 135
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 1161 | 3483
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1787.4144
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 103.33 | 537.316
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 103.33 | 257.4984
| 2601 00 0027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1787.4144
10 |  | COST OF MATERIALS |  |  |  | 54974.2264
11 |  | A |  |  |  | 54974.2264
|  | ADD:3% CONTINGENCIES |  |  |  | 1649.2268
|  | ADD:2% STORAGE CHARGES |  |  |  | 1099.4845
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1099.4845
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8246.134
|  | Total ….A |  |  |  | 67068.5562
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 271 | 542
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 250
13 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON RSJ POLE,HG FUSE | SET | 1 | 2734 | 2734
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 486 | 972
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 422 | 1688
ACCESSORIES & FITTINGS.
14 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
15 |  | LABOUR CHARGES |  |  |  | 9737.4
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1460.61
17 |  | B |  |  |  | 11198.01
18 |  | Sub Total(A+B) |  |  |  | 78266.5662
|  | Total Estimate |  |  | Say Rs. | 78266.5662

## H14.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 14
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 55MM2 AAA CONDUCTOR USING 8 MTR/ 200 KG PSC POLES. WPZ - 100 KG/M2(SPAN 50 MTRS.)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2820.2 | 56404
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 787 | 15740
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1194.748 | 2389.496
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
[6 empty] | 1194.748 | 0
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
|  | Material required for 1 No earthing |  |  |  |  | 0
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 199.24 | 11954.4
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL. |  | 12 | 416.73 | 5000.76
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4145.6758
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 103.33 | 1198.628
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.66 | 103.33 | 1618.1478
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 112.1 | 1008.9
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
4145.6758
14 |  | COST OF MATERIALS |  |  |  | 234863.1118
15 |  | A |  |  |  | 234863.1118
|  | ADD:3% CONTINGENCIES |  |  |  | 7045.8934
|  | ADD:2% STORAGE CHARGES |  |  |  | 4697.2622
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4697.2622
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 35229.4668
|  | Total ….A |  |  |  | 286532.9964
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 271 | 5420
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 878 | 17560
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 422 | 844
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5919 | 1775.7
24 |  | LABOUR CHARGES |  |  |  | 41170.7
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6175.605
26 |  | B |  |  |  | 47346.305
27 |  | Sub Total(A+B) |  |  |  | 333879.3014
|  | Total Estimate |  |  | Say Rs. | 333879.3014

## H15.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 15
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-33 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 30 | 18428 | 552840
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 787 | 23610
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 199.24 | 17931.6
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
11 |  | 11KV STRAIN INSULATOR COMPL. |  | 24 | 416.73 | 10001.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6008.304
14 |  | COST OF MATERIALS |  |  |  | 764430.892
15 |  | A |  |  |  | 764430.892
|  | ADD:3% CONTINGENCIES |  |  |  | 22932.9268
|  | ADD:2% STORAGE CHARGES |  |  |  | 15288.6178
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 15288.6178
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 114664.6338
|  | Total ….A |  |  |  | 932605.6882
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 271 | 8130
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1395 | 41850
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5919 | 126074.7
24 |  | LABOUR CHARGES |  |  |  | 199017.7
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 29852.655
26 |  | B |  |  |  | 228870.355
27 |  | Sub Total(A+B) |  |  |  | 1161476.0432
|  | Total Estimate |  |  | Say Rs. | 1161476.0432

## H16.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 16
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-50 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 20 | 18428 | 368560
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 787 | 15740
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 199.24 | 11954.4
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 416.73 | 10001.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6008.304
14 |  | COST OF MATERIALS |  |  |  | 558661.492
15 |  | A |  |  |  | 558661.492
|  | ADD:3% CONTINGENCIES |  |  |  | 16759.8448
|  | ADD:2% STORAGE CHARGES |  |  |  | 11173.2298
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11173.2298
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 83799.2238
|  | Total ….A |  |  |  | 681567.0202
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 271 | 5420
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1395 | 27900
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF RSJ & GUY WITH MATERIAL(1:2:4) | CMT | 14.5 | 5919 | 85825.5
24 |  | LABOUR CHARGES |  |  |  | 137248.5
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 20587.275
26 |  | B |  |  |  | 157835.775
27 |  | Sub Total(A+B) |  |  |  | 839402.7952
|  | Total Estimate |  |  | Say Rs. | 839402.7952

## H17.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 17
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE- 9 MTR (SPAN-50 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*9 MTR | NO. | 20 | 15077 | 301540
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 787 | 15740
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 199.24 | 11954.4
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 416.73 | 10001.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6008.304
14 |  | COST OF MATERIALS |  |  |  | 491641.492
15 |  | A |  |  |  | 491641.492
|  | ADD:3% CONTINGENCIES |  |  |  | 14749.2448
|  | ADD:2% STORAGE CHARGES |  |  |  | 9832.8298
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 9832.8298
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 73746.2238
|  | Total ….A |  |  |  | 599802.6202
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 271 | 5420
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1395 | 27900
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776 | GUY .15
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 14.5 | 5919 | 85825.5 | 14.5
24 |  | LABOUR CHARGES |  |  |  | 137248.5
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 20587.275
26 |  | B |  |  |  | 157835.775
27 |  | Sub Total(A+B) |  |  |  | 757638.3952
|  | Total Estimate |  |  | Say Rs. | 757638.3952

## H18.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 18
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON PSC POLE(SPAN-33 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 30 | 2820.2 | 84606
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 787 | 23610
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 199.24 | 17931.6
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 199.24 | 199.24
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
199.24
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 416.73 | 10001.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 39982 | 123544.38
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 7681.2167
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 19 | 103.33 | 1963.27
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 25.99 | 103.33 | 2685.5467
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
7681.2167
14 |  | COST OF MATERIALS |  |  |  | 295480.3087
15 |  | A |  |  |  | 295480.3087
|  | ADD:3% CONTINGENCIES |  |  |  | 8864.4093
|  | ADD:2% STORAGE CHARGES |  |  |  | 5909.6062
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5909.6062
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 44322.0463
|  | Total ….A |  |  |  | 360485.9766
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF PSC POLES AT DESTI. | NO. | 30 | 271 | 8130
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 878 | 26340
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1592 | 4776
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 422 | 1688
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5919 | 3551.4
24 |  | LABOUR CHARGES |  |  |  | 60140.4
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9021.06
30
26 |  | B |  |  |  | 69161.46
27 |  | Sub Total(A+B) |  |  |  | 429647.4366
|  | Total Estimate |  |  | Say Rs. | 429647.4366

## H19.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 19
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (33 MTR. SPAN)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 30 | 18428 | 552840
2 | 26 09 00 0034 | 22KV V CROSS ARM. | NO. | 30 | 1021 | 30630
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 91 | 2730
| 26 01 00 0049 | Side clamp | No | 30 | 91 | 2730
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 160 | 4800
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 333.22 | 9996.6
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 22KV PIN INSULATOR COMPL. | NO. | 90 | 0 | 0
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 1 | 0 | 0
| 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 1 | 0 | 0
0
11 |  | 22KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 551.73 | 13241.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 135 | 270
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
551.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 73163 | 226073.67
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6008.304
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 103.33 | 2975.904
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 112.1 | 2690.4
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6008.304
14 |  | COST OF MATERIALS |  |  |  | 859288.582
15 |  | A |  |  |  | 859288.582
|  | ADD:3% CONTINGENCIES |  |  |  | 25778.6575
|  | ADD:2% STORAGE CHARGES |  |  |  | 17185.7716
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 17185.7716
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 128893.2873
|  | Total ….A |  |  |  | 1048332.07
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 271 | 8130
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1395 | 41850
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 3668 | 11004
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 486 | 14580
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5919 | 126074.7
24 |  | LABOUR CHARGES |  |  |  | 205245.7
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 30786.855
26 |  | B |  |  |  | 236032.555
27 |  | Sub Total(A+B) |  |  |  | 1284364.625
|  | Total Estimate |  |  | Say Rs. | 1284364.625

## H20.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 20
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (50 MTR SPAN)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 20 | 18428 | 368560
2 | 26 09 00 0034 | 22KV V CROSS ARM. | NO. | 20 | 1021 | 20420
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 91 | 1820
| 26 01 00 0049 | Side clamp | No | 20 | 91 | 1820
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 160 | 3200
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 200 | 400
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 200 | 400
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 333.22 | 6664.4
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 84.19 | 252.57
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 80.65 | 80.65
333.22
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 22KV PIN INSULATOR COMPL. | NO. | 60 | 0 | 0
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 1 | 0 | 0
| 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 1 | 0 | 0
0
11 |  | 22KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 551.73 | 13241.52
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 135 | 270
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
551.73
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 73163 | 226073.67
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 342
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 0 | 103.33 | 0
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 103.33 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 0 | 112.1 | 0
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
342
14 |  | COST OF MATERIALS |  |  |  | 651490.078
15 |  | A |  |  |  | 651490.078
|  | ADD:3% CONTINGENCIES |  |  |  | 19544.7023
|  | ADD:2% STORAGE CHARGES |  |  |  | 13029.8016
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 13029.8016
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 97723.5117
|  | Total ….A |  |  |  | 794817.8952
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 475
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 271 | 5420
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 600
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1395 | 27900
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 3668 | 11004
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 422 | 2532
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 486 | 9720
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 14.5 | 5919 | 85825.5
24 |  | LABOUR CHARGES |  |  |  | 143476.5
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 21521.475
26 |  | B |  |  |  | 164997.975
27 |  | Sub Total(A+B) |  |  |  | 959815.8702
|  | Total Estimate |  |  | Say Rs. | 959815.8702

## H21.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 21
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV RAILWAY CROSSING BY 185 MM2 U/G XLPE CABLE. ( DOUBLE CKT 115 MTR LENGTH)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 36 04 00 0001 | RSJ 116*100 MM 9 MTR. | NO. | 4 | 15077 | 60308
2 | 26 09 00 0034 | V CROSS ARMS 11KV | NO. | 4 | 787 | 3148
3 |  | STRAIN INSULATOR 11 KV WITH H/W | SET | 6 | 416.73 | 2500.38
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 281.73 | 281.73
416.73
4 | 04 05 00 0009 | 11 KVXLPE CABLE 3 CORE 185 mm2 SIZE.(Double CKT) | MTR | 230 | 1039.58 | 239103.4
5 |  | ANTI-CLIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | No | 2 | 120 | 240
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1194.748 | 7168.488
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
8 |  | SUNDRY MATERIAL SUCH AS |  |  |  | 1723.912
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6.4 | 103.33 | 661.312
| 19 05 00 0006 | (b) HT Binding Tape | Mtr | 30 | 13 | 390
| 2601 00 0027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
1723.912
9 |  | COST OF MATERIALS |  |  |  | 314312.18
10 |  | A |  |  |  | 314312.18
|  | ADD:3% CONTINGENCIES |  |  |  | 9429.3654
|  | ADD:2% STORAGE CHARGES |  |  |  | 6286.2436
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 6286.2436
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 47146.827
|  | Total ….A |  |  |  | 383460.8596
11 |  | LABOUR CHARGES FOR COMPLETE |  |  | ----LS---- | 350000
WORK OF CROSSING
(INCLUDING LAYING, JOINTING, INSERTATIOIN OF 150MM DIA C. I. PIPE UNDER RAILWAY TRACK USING HORIZONTAL AUGER GUIDED BORING BY PUSH THROUGH METHOD; INSERTATION OF C. I. PIPE IN SIDE RAILWAY BOUNDRY BY CUT AND FILL METHOD; PROVIDING AND SUPPLY OF 150MM DIA C. I. PIPE; LAYING OF 11KV XLPE CABLE IN SIDE C. I. PIPE; PROVIDING SUPPLY AND FIXING 185MM2 CABLE BOX, TERMINATION KIT; PROVIDING PAINTING, FABRICATION AND FIXING OF CABLE MARKER; PROVIDING AND FIXING OF G. I, PIPE ON ERECTED STRUCTURE FOR MECHANICAL PROTECTION OF XLPE CABLE & PROVIDING EARTHING AS PER RAILWAY AUTHORITY ETC.) THE FOLLOWING ITEMS ARE COVERED IN THE SCOPE OF SUPPLIER/CONTRACTOR. LENGTH OF CI PIPE, EARTHING, ITS INSTALLATION EVERYTHING BETWEEN TWO END TERMINATION ACROSS THE RAILWAY TRACK SHALL BE ACCORDING TO DRAWING APPROVED BY CONCERN RAILWAY AUTHORITY. CABLE WILL BE CARTED FROM STORE TO SITE BY CONTRACTOR. ONLY CABLE WILL BE PROVIDED BY UGVCL.
12 |  | CARTING OF RSJ POLE AT DEST. | NO. | 2 | 271 | 542
13 |  | CARTING OF LINE MATERIAL AT |  |  | ----LS---- | 600
WORK SITE
14 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 2.26 | 5919 | 13376.94
15 |  | LABOUR CHARGES |  |  |  | 364518.94
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 54677.841
17 |  | B |  |  |  | 419196.781
18 |  | Sub Total(A+B) |  |  |  | 802657.6406
|  | Total Estimate |  |  | Say Rs. | 802657.6406

## H22.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 22
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
GUARDING FOR H.T./ L.T.LINES AND P&T LINES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | GUARDING ANGLE CROSS ARM | NO. | 2 | 857 | 1714
| 26 09 00 0029/ 31 | M.S.Angle 65x65x6mm - 2 Mtr for Guarding Angle cross arm/Guarding channel | No | 2 | 857 | 1714
2 |  | BACK CLAMP | NO. | 2 | 91 | 182
| 26 01 00 0049 | Side clamp | No | 2 | 91 | 182
3 | 01 03 00 0003 | G.I. WIRE 10 SWG | KG. | 2 | 84.19 | 168.38
4 | 01 03 00 0002 | G.I. WIRE NO. 8 | KG. | 14 | 84.19 | 1178.66
5 |  | MISC. ITEMS i.e.BOLTS ,NUTS |  |  |  | 402.664
WASHER,BINDING WIRES.
| 26 14 00 0012 | Eye-bolt | No | 4 | 74 | 296
| 15 01 00 0024 | Bolts & Nuts - 65x16mm | KG | 0.8 | 103.33 | 82.664
| 01 01 00 0003 | Alu.Binding wire | KG | 0.2 | 120 | 24
402.664
6 |  | COST OF MATERIALS |  |  |  | 3645.704
7 |  | A |  |  |  | 3645.704
|  | ADD:3% CONTINGENCIES |  |  |  | 109.3711
|  | ADD:2% STORAGE CHARGES |  |  |  | 72.9141
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 72.9141
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 546.8556
|  | Total ….A |  |  |  | 4447.7589
8 |  | LABOUR CHARGES FOR FIXING | NO. | 2 | 363 | 726
OF CROSS ARMS ON LOCATION.
9 |  | PROVIDE GUARDING. | MTR | 60 | 58 | 3480
COMPLETE WITH PAINTING.
10 |  | LABOUR CHARGES |  |  |  | 4206
11 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 630.9
12
13 |  | B |  |  |  | 4836.9
14 |  | Sub Total(A+B) |  |  |  | 9284.6589
|  | Total Estimate |  |  | Say Rs. | 9284.6589

## H23.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 23
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2820.2 | 5640.4
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 16740
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 1850 | 3700
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
16740
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 486.84 | 1460.52
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | HT SMC Box | NO. | 1 | 3014.1 | 3014.1
10 |  | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 5 | 331 | 1655
| 04 01 00 0004 | Doble Compressed 25 mm2 Cable Gland | No. | 0 | 135 | 0
|  | Test Terminal Box | No. | 1 | 875 | 875
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 0 | 108.97 | 0
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 0 | 108.97 | 0
12 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 1078.21 | 1078.21
| 1607000009 | (i) 3-ph MMB | NO | 1 | 896.21 | 896.21
| 2601000061 | (ii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
1078.21
13 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3277.0245
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/ 28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 18 | 54
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 5 | 10
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3277.0245
14 |  | COST OF MATERIALS |  |  |  | 43919.2465
15 |  | A |  |  |  | 43919.2465
|  | ADD:3% CONTINGENCIES |  |  |  | 1317.5774
|  | ADD:2% STORAGE CHARGES |  |  |  | 878.3849
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 878.3849
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 6587.887
|  | Total ….A |  |  |  | 53581.4807
16 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
17 |  | DIST.BOX ETC. | NO. | 1 | 6814 | 6814
18 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
19 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
20 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
21 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
23 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
24 |  | LABOUR CHARGES… |  |  |  | 23253.24
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3487.986
26 |  | B |  |  |  | 26741.226
27 |  | Sub Total(A+B) |  |  |  | 80322.7067
|  | Total Estimate |  |  | Say Rs. | 80322.7067

## H24.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 24
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 11 MTR RSJ POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 11 Meter | NO. | 2 | 18428 | 36856
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | NO. | 1 | 15400 | 15400
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 1180 | 2360
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
15400
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 486.84 | 1460.52
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | HT SMC Box | NO. | 1 | 3014.1 | 3014.1 | check
10 |  | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 5 | 331 | 1655
| 04 01 00 0004 | Doble Compressed 25 mm2 Cable Gland | No. | 2 | 135 | 270
|  | Test Terminal Box | No. | 1 | 875 | 875
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 0 | 108.97 | 0
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 0 | 108.97 | 0
12 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 1078.21 | 1078.21
| 1607000034 | (i) 3-ph SMC Box | NO | 1 | 896.21 | 896.21
| 2601000061 | (ii) SIDE CLAMPS (50x6mm) | NO | 2 | 91 | 182
1078.21
13 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3277.0245
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 26 01 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 18 | 54
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 5 | 10
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3277.0245
14 |  | COST OF MATERIALS |  |  |  | 74064.8465
15 |  | A |  |  |  | 74064.8465
|  | ADD:3% CONTINGENCIES |  |  |  | 2221.9454
|  | ADD:2% STORAGE CHARGES |  |  |  | 1481.2969
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1481.2969
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 11109.727
|  | Total ….A |  |  |  | 90359.1127
16 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
17 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
18 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
19 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
20 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
22 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
23 |  | LABOUR CHARGES… |  |  |  | 24028.24
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3604.236
25 |  | B |  |  |  | 27632.476
26 |  | Sub Total(A+B) |  |  |  | 117991.5887
|  | Total Estimate |  |  | Say Rs. | 117991.5887

## H25.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 25
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 9 MTR RSJ POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 9 Meter | NO. | 2 | 15077 | 30154
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | NO. | 1 | 15400 | 15400
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 2249 | 8996
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 1180 | 2360
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 1180 | 2360
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 318 | 1272
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 412 | 412
15400
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 1161 | 3483
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 519 | 1557
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1194.748 | 4778.992
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 486.84 | 1460.52
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 80.65 | 80.65
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 84.19 | 84.19
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | HT SMC Box | NO. | 1 | 3014.1 | 3014.1
10 |  | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 5 | 331 | 1655
| 04 01 00 0004 | Double Compressed 25 mm2 Cable Gland | No. | 2 | 135 | 270
|  | Test Terminal Box | No. | 0 | 875 | 0
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 0 | 108.97 | 0
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 0 | 108.97 | 0
12 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 0 | 0 | 0
| 1607000034 | (i) 3-ph SMC Box | NO | 0 | 896.21 | 0
| 2601000061 | (ii) SIDE CLAMPS (50x6mm) | NO | 0 | 91 | 0
0
13 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3277.0245
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 103.33 | 413.32
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 103.33 | 367.8548
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 103.33 | 319.2897
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 18 | 54
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.76 | 4.56
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 0 | 0.76 | 0
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 5 | 10
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 4 | 24
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 4 | 8
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 43 | 258
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 91 | 1092
3277.0245
14 |  | COST OF MATERIALS |  |  |  | 65409.6365
15 |  | A |  |  |  | 65409.6365
|  | ADD:3% CONTINGENCIES |  |  |  | 1962.2891
|  | ADD:2% STORAGE CHARGES |  |  |  | 1308.1927
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1308.1927
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 9811.4455
|  | Total ….A |  |  |  | 79799.7565
16 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 7589 | 7589
17 |  | ERECTION OF EARTHING COIL | NO. | 3 | 486 | 1458
PLATE TYPE WITH SALT &COAL
18 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 422 | 1688
19 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 271 | 542
20 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 600
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5919 | 11601.24
22 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
23 |  | LABOUR CHARGES… |  |  |  | 24028.24
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3604.236
25 |  | B |  |  |  | 27632.476
26 |  | Sub Total(A+B) |  |  |  | 107432.2325
|  | Total Estimate |  |  | Say Rs. | 107432.2325

## H26.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 26
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
RIVER CROSSING USING 10 MTR PSC POLES FOR 11KV
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10Mtr. (270KG) | NO. | 4 | 5136.54 | 20546.16
2 |  | TOP CROSS ARMS FOR TERMINATING | NO. | 4 | 1180 | 4720
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750 mm for top cross arm for terminating line | No | 4 | 1180 | 4720
3 |  | BRACING FOR DOUBLE POLENSTRUCTURE | SET | 2 | 4720 | 9440
( 4 angles perset)
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV | No. | 4 | 1180 | 4720
4 |  | 11 KV STRAIN INSULATOR H/W WITH | SET | 12 | 416.73 | 5000.76
PREFORMED FITTING
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
5 |  | ANTI-CLIMBING DEVICES. | NO. | 4 | 120 | 480
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 4 | 120 | 480
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 4 | 60 | 240
7 |  | EARTHING OF D.P. STRUCTURE | NO. | 4 | 486.84 | 1947.36
Material required for 1 No. Pipe Type earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 1 Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (e) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (f) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | GUY SET WITH PREFORMED FITTING | NO. | 8 | 1194.748 | 9557.984
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
9 |  | SUNDRY MATERIAL SUCH AS BOLT & |  |  |  | 1837.1674
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 103.33 | 495.984
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 4.98 | 103.33 | 514.5834
| 26 01 00 0027/0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 19 05 00 0006 | (d) HT Tape for binding | Mtr | 10 | 13 | 130
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.2 | 120 | 24
1837.1674
10 |  | COST OF MATERIALS |  |  |  | 53769.4314
11 |  | A |  |  |  | 53769.4314
|  | ADD:3% CONTINGENCIES |  |  |  | 1613.0829
|  | ADD:2% STORAGE CHARGES |  |  |  | 1075.3886
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1075.3886
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8065.4147
|  | Total ….A |  |  |  | 65598.7063
12 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE . | NO. | 2 | 4433 | 8866
13 |  | INSTALLATION OF EARTHING COIL | NO. | 4 | 486 | 1944
PLATE TYPE WITH SALT &COAL
14 |  | PROVIDING GUY SET COMP.WITH | NO. | 8 | 422 | 3376
ALL ACCESSORES &FITTING
15 |  | CARTING OF PSC POLE AT DEST. | NO. | 4 | 450 | 1800
16 |  | CARTING OF MATERIAL AT WORK SITE |  |  | ----LS---- | 600
17 |  | CONCRETING OF GUY & RSJ POLES WITH MATERIAL(1:2:4) | CMT | 1.2 | 5919 | 7102.8
18 |  | LABOUR CHARGES.. |  |  |  | 23688.8
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3553.32
20 |  | B |  |  |  | 27242.12
21 |  | Sub Total(A+B) |  |  |  | 92840.8263
|  | Total Estimate |  |  | Say Rs. | 92840.8263

## H27.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 27
COST DATA FOR HT POWER SUPPLY FOR FY 2022-23
RIVER CROSSING USING 11 MTR RSJ POLES FOR 11KV
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*100*11 Meter | NO. | 4 | 18428 | 73712
2 |  | TOP CROSS ARMS FOR TERMINATING | NO. | 4 | 1180 | 4720
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750 mm for top cross arm for terminating line | No | 4 | 1180 | 4720
3 |  | BRACING FOR DOUBLE POLENSTRUCTURE | SET | 2 | 4720 | 9440
( 4 angles perset)
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV | No. | 4 | 1180 | 4720
4 |  | 11 KV STRAIN INSULATOR H/W WITH | SET | 12 | 416.73 | 5000.76
PREFORMED FITTING
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 1 | 135 | 135
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 1 | 281.73 | 281.73
416.73
5 |  | ANTI-CLIMBING DEVICES. | NO. | 4 | 120 | 480
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 4 | 120 | 480
30.192
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 4 | 60 | 240
7 |  | EARTHING OF D.P. STRUCTURE | NO. | 4 | 486.84 | 1947.36
Material required for 1 No. Pipe Type earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 1 Kg | KG | 1 | 84.19 | 84.19
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 80.65 | 80.65
| 09 01 00 0007 | (e) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (f) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
486.84
8 |  | GUY SET WITH PREFORMED FITTING | NO. | 8 | 1194.748 | 9557.984
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 260 | 260
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 170.628 | 170.628
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 88.61 | 443.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 42.07 | 42.07
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 200 | 200
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1194.748
9 |  | SUNDRY MATERIAL SUCH AS BOLT & |  |  |  | 1735.1674
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 103.33 | 495.984
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 4.98 | 103.33 | 514.5834
| 26 01 00 0027/0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 112.1 | 672.6
| 19 05 00 0006 | (d) HT Tape for binding | Mtr | 10 | 2 | 20
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.2 | 160 | 32
1735.1674
10 |  | COST OF MATERIALS |  |  |  | 106833.2714
11 |  | A |  |  |  | 106833.2714
|  | ADD:3% CONTINGENCIES |  |  |  | 3204.9981
|  | ADD:2% STORAGE CHARGES |  |  |  | 2136.6654
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2136.6654
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 16024.9907
|  | Total ….A |  |  |  | 130336.5911
12 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON RSJ POLE . | NO. | 2 | 2734 | 5468
13 |  | INSTALLATION OF EARTHING COIL | NO. | 4 | 486 | 1944
PLATE TYPE WITH SALT &COAL
14 |  | PROVIDING GUY SET COMP.WITH | NO. | 8 | 422 | 3376
ALL ACCESSORES &FITTING
15 |  | CARTING OF RSJ POLE AT DEST. | NO. | 4 | 271 | 1084
16 |  | CARTING OF MATERIAL AT WORK SITE |  |  | ----LS---- | 600
17 |  | CONCRETING OF GUY & RSJ POLES WITH MATERIAL(1:2:4) | CMT | 3.92 | 5919 | 23202.48
18 |  | LABOUR CHARGES.. |  |  |  | 35674.48
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 5351.172
20 |  | B |  |  |  | 41025.652
21 |  | Sub Total(A+B) |  |  |  | 171362.2431
|  | Total Estimate |  |  | Say Rs. | 171362.2431