## Front
UGVCL
Cost Data & Labour Rates
2019-20

## Labour Rate (hidden)
APPROVED LABOUR RATES FOR WORKS FOR THE YEAR 2019-20
Sr. No | Name | Unit | 2012-13 | 2014-15 | 2015-16 | Approved rate 2019-20 | Diff of FY15-16 | % Rise
1 | SURVEY,TREE CUTTING &COMPENSATION | ----LS---- | 115 | 145 | 160 | 400 | 240 | 150% | 400
2 | CARTING OF LINE MATERIALS TO SITE FOR AB SWITCH/ MISC | ----LS---- | 160 | 200 | 220 | 230 | 10 | 4.545% | 230
3 | CARTING OF LINE MATERIALS TO SITE FOR TC/LINE | ---LS--- | 390 | 500 | 550 | 575 | 25 | 4.545% | 575
4 | STRINGING OF CONDUCTOR | KM. | 885 | 1130 | 1240 | 1373 | 133 | 10.73% | 1373
5 | STRINGING OF DOG CONDUCTOR. | KM. | 1950 | 2490 | 2730 | 3162 | 432 | 15.82% | 3162
6 | ERECTION OF GUY SET COMPLETE | NO. | 225 | 288 | 315 | 364 | 49 | 15.56% | 364
7 | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 6 | 7.7 | 8.5 | 9 | 0.5 | 5.882% | 9
8 | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 4200 | 5375 | 5900 | 5900 | 0 | 0% | 5900
9 | LABOUR CHARGES FOR ERECTION OF T/C.INCL. | NO. | [6 empty] | 0
| PAINTINGING OF STRUCTURE MATERIAL AND | [7 empty] | 0
| PROVIDING LIGHTENING ARRESTOR,HG FUSES, | [7 empty] | 0
| DIST.BOX ETC. ON Single Pole Stucture |  | 2030 | 2600 | 2860 | 2949 | 89 | 3.112% | 2949
10 | LABOUR CHARGES FOR ERECTION OF T/C.INCL. | NO. | [6 empty] | 0
| PAINTINGING OF STRUCTURE MATERIAL AND | [7 empty] | 0
| PROVIDING LIGHTENING ARRESTOR,HG FUSES, | [7 empty] | 0
| DIST.BOX ETC. on duble Pole Structure (8* mtr) |  | 3815 | 4880 | 5360 | 5900 | 540 | 10.07% | 5900 |  | DIST.BOX ETC. on duble Pole Structure (10* mtr)
11 | LABOUR CHARGES FOR ERECTION OF T/C.INCL. | NO. | [6 empty] | 0
| PAINTINGING OF STRUCTURE MATERIAL AND | [7 empty] | 0
| PROVIDING LIGHTENING ARRESTOR,HG FUSES, | [7 empty] | 0
| DIST.BOX ETC. on Plinth / RSJ Pole |  | 5285 | 5600 | 6160 | 6899 | 739 | 12% | 6899
12 | ERECTION OF EARTHING COIL | NO. | 250 | 320 | 350 | 419 | 69 | 19.71% | 419
| PLATE TYPE WITH SALT &COAL | [7 empty] | 0
13 | CARTING OF POLE AT WORK SITE | NO. | 160 | 200 | 220 | 246 | 26 | 11.82% | 246
14 | CARTING OF POLE AT DEST. 10 Mtr | NO. | 225 | 290 | 320 | 400 | 80 | 25% | 400
13 | CARTING OF RSJ POLE AT DESTINATION | NO. | 160 | 200 | 220 | 246 | 26 | 11.82% | 246
14 | LABOUR CHARGES FOR LAYING OF | No | 230 | 295 | 325 | 355 | 30 | 9.231% | 355
| 3 PHASE SERVICE CONNECTION | [7 empty] | 0
15 | LABOUR CHARGES FOR | NO. | 480 | 615 | 675 | 757 | 82 | 12.15% | 757
| ERECTION OF PSC POLE INCLUDING | [7 empty] | 0
| DIGGING OF PITS, FIXING OF POLE | [7 empty] | 0
| FIXTURE etc. AND PAINTING OF | [7 empty] | 0
| STEEL FIXTURE. | [7 empty] | 0
16 | LABOUR CHARGES FOR ERECTION | NO. | 800 | 1020 | 1120 | 1268 | 148 | 13.21% | 1268
| OF RSJ POLE INCLUDING DIGGING. | [7 empty] | 0
| OF PITS,FIXING OF POLES FIXTURE, | [7 empty] | 0
| INSULATOR & PAINTING STEEL POLE | [7 empty] | 0
17 | LABOUR CHARGES FOR ERECTION 10 Mtr | NO. | 1295 | 1650 | 1815 | 1815 | 0 | 0% | 1815
| OF PSC POLE INCLUDING DIGGING. | [7 empty] | 0
| OF PITS,FIXING OF POLES FIXTURE, | [7 empty] | 0
| INSULATOR & PAINTING STEEL POLE | [7 empty] | 0
18 | INSTALLATION OF ENERGY METER,MM BOX ETC. | ---LS--- | 395 | 500 | 550 | 550 | 0 | 0% | 550
| ON T/C | [7 empty] | 0
19 | LABOUR CHARGES FOR PROVIDING STREET | ---L.S--- | 150 | 192 | 210 | 227 | 17 | 8.095% | 227
| LIGHT FIXURE | [7 empty] | 0
20 | PLINTH (3.34*3.34*1.5MTR) FOR MOUNTING X-MER | ---LS--- | 75000 | 96000 | 105600 | 65715.44 | -39884.56 | -37.77% | 65715.44 | Rate of CMT 3928/-cmt |  | MEHSANA SOR GIVEN BY CIVIL SECTION
21 | LABOUR CHARGES FOR ERECTION OF D.O on Single Pole | SET | [6 empty] | 0
| STRUCTURE ON PSC POLE,HG FUSE |  | 1285 | 820 | 905 | 905 | 0 | 0% | 905
21 | LABOUR CHARGES FOR ERECTION OF D.P. | SET | [6 empty] | 0
| STRUCTURE ON PSC POLE,HG FUSE |  | 1285 | 1645 | 1810 | 2067 | 257 | 14.2% | 2067
22 | LABOUR CHARGES FOR ERECTION OF D.P. | SET | [6 empty] | 0
| STRUCTURE ON RSJ POLE WITH | [7 empty] | 0
| AB SWITCH/HG FUSE |  | 1660 | 2125 | 2335 | 2485 | 150 | 6.424% | 2485
23 | LABOUR CHARGES FOR ERECTION OF D.P. | SET | [6 empty] | 0
| STRUCTURE ON PSC POLE 10 mtr ,HG FUSE |  | 2865 | 3665 | 4030 | 4030 | 0 | 0% | 4030
24 | LABOUR CHARGES FOR COMPLETE | ----LS---- | 380000 | 486000 | 534000 | 350000 | -184000 | -34.46% | 350000
| WORK OF UNDERGROUND RIVER CROSSING | [7 empty] | 0
25 | LABOUR CHARGES FOR FIXING (Tapping) | NO. | [6 empty] | 0
| OF CROSS ARMS, BRACING ON LOCATION |  | 135 | 172 | 278 | 313 | 35 | 12.59% | 313
26 | PROVIDE GUARDING. | MTR | 42 | 53 | 58 | 58 | 0 | 0% | 58
| COMPLETE WITH PAINTING. | [7 empty] | 0
| LABOUR CHARGES | [7 empty] | 0
27 | LABOUR CHARGES FOR PROVIDING FANCING | ---LS--- | 3350 | 4275 | 4700 | 4700 | 0 | 0% | 4700
| AROUND DIST. TRANSFORMER CENTER | [7 empty] | 0
28 | HINGERS, STOPPERS (Lump Sump) | ---LS--- | 550 | 700 | 770 | 770 | 0 | 0% | 770
29 | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR | ---LS--- | 450 | 575 | 630 | 630 | 0 | 0% | 630
30 | Labour charge for laying U/G XLPE cable including digging of pit (4 Ft.) and laying of cable with providing Cable Trench with bricks & send providing of cable indicator | MTR. | 220 | 280 | 305 | 335 | 30 | 9.836% | 335
31 | LABOUR CHARGES FOR COMPLETE | ----LS---- | [6 empty] | 0
| WORK OF Railway CROSSING |  | 435000 | 556800 | 612000 | 350000 | -262000 | -42.81% | 350000
32 | Stringing of of three phase(HT) AB Cable including fittings of All Accessories | KM | New | 10000 | 11000 | 28994 | 17994 | 163.6% | 28994
| Stringing of of three phase 4 wisre (LT 3P4W) AB Cable including fittings of All Accessories |  |  |  |  | 14707 | 14707 | #DIV/0! |  | New Item
33 | Stringing of of single phase AB Cable(LT 1P2W) including fittings of All Accessories | KM | New | 4000 | 4400 | 5883 | 1483 | 33.7% | 5883
33 | Crimping Of Insulated Mid Span Joint For ABC | NO | New | 10 | 11 | 11 | 0 | 0% | 11
34 | ERECTION OF EARTHING CHAMBER | NO |  | 2000 | 2000 | 2000 | 0 | 0% | 2000
| EXCAVATION OF EART PIT SALT, CHARCOAL & BENTONITE | [7 empty] | 0
35 | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR |  | 30 | 30 | 30 | 0 | 0% | 30
| DP STRUCTURE WITH XMER ON 10 MTR PSC POLE |  |  |  |  | 6900
36 | PROVIDING SINGLE PHASE SERVICE CONNECTION |  |  |  |  | 258
37 | Replacement of 1 Ph old service line by new PVC/Armored service line |  |  |  |  | 170
| Replacement of 1 Ph meter box without meter |  |  |  |  | 50
| Replacement of 1 Ph meter only (Rural Area) by another one. |  |  |  |  | 45
| ERECTION OF DOUBLE POLE STRUCTURE OF 10 METERS 200 KG PSC POLES |  |  |  |  | 4030
| Providing & Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 160 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. |  |  |  |  | 1440
| Providing and Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 110 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. |  |  |  |  | 1350

## Annexure-E
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM WISE COST DATA (RE/CITY) FOR FY 2019-20
ANNEXURE-E
SR NO. | ITEM CODE | ITEM NO | PARTICULARS | UNIT | RATE OF 2012-13 | RATE OF 2014-15 | RATE OF 2015-16 | RATE (In Rs.) | % Variation
1 | 9601000001 | ITEM 1 | TAPPING FROM EXISTING POLES FOR 11 KV LINE | NO | 5529.4508 | 6235.5375 | 5918 | 6498 | 9.801%
2 | 9601000002 | ITEM 2 | GUARDING UNDER HT AND LT LINE (SPAN-60 MTR) | NO | 6120.7864 | 7392.228 | 7518 | 8238 | 9.577%
3 | 9601000003 | ITEM 3 | 11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 8 MTR POLE | NO | 31405.8152 | 36033.4172 | 36744 | 38929 | 5.947%
4 | NEW | ITEM 4 | 11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 10 MTR POLE | NO |  |  |  | 45171
5 | 9602000104 | ITEM 5 | 11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH On RSJ 9 MTR POLE | NO | 49556.3452 | 57552.3372 | 55216 | 70233 | 27.2%
6 | 9601000004 | ITEM 6 | 11 KV DOUBLE POLE STRUCTURE WITH HG FUSE (WITHOUT AB SWITCH) On PSC 8 MTR POLE | NO | 27824.5052 | 31884.1972 | 31223 | 31950 | 2.328%
HT LINE
7 | 9601000005 | ITEM 7 | 11KV LINE WITH 34 MM2 AAAC CONDUCTOR( SPAN 50 MTR ) ON 8 MTR PSC POLE WITH WIND PRESSURE ZONE 100 KG/M2 | KM | 181976.2276 | 205025.3684 | 210114 | 222012 | 5.663%
8 | 9601000006 | ITEM 8 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 | KM | 219655.7446 | 243352.3973 | 251371 | 264766 | 5.329%
9 | 9602000204 | ITEM 9 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 | KM | 282848.1572 | 316698.2737 | 321505 | 341479 | 6.213%
10 | 9602000207 | ITEM 10 | 11KV LINE WITH DOG CONDUCTOR (SPAN-50 MTR) ON PSC POLE (10 MTR) WITH 11 KV MATERIALS | KM | 381803.0524 | 427643.704 | 441438 | 445371 | 0.891%
11 | NEW | ITEM 11 | 11KV LINE WITH DOG CONDUCTOR (SPAN-33 MTR) ON PSC POLE (10 MTR) WITH 11 KV MATERIALS | KM |  |  |  | 546157
12 | 9602000208 | ITEM 12 | 11KV LINE WITH DOG AAAC CONDUCTOR (SPAN-33 MTR) ON RSJ POLE (9 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 771086.4964 | 887812.7126 | 875431 | 928282 | 6.037%
13 | 9602000209 | ITEM 13 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-50 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS | KM | New | 307169.3973 | 310660 | 328790 | 5.836%
14 |  | ITEM 14 | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS | KM |  |  |  | 432006
15 | 9601000007 | ITEM 15 | UNDER GROUND RAILWAY CROSSING (DOUBLE TRACK- BROAD GAUGE) FOR 11 KV SYSTEM | NO | 667430.5248 | 798129.8646 | 863261 | 775184 | -10.2%
16 | 9601000008 | ITEM 16 | RIVER CROSSING (11KV) on 10 MTR PSC POLE | NO | 60713.8332 | 73308.5788 | 70862 | 73938 | 4.341%
TRANSFORMER CENTRE ON SINGLE POLE STRUCTURE WITHOUT FENCING
17 | 9601000026 | ITEM 17 | 25 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO | 111042.7684 | 108778.9301 | 111847 | 109370 | -2.215%
18 | 9601000044 | ITEM 18 | 16 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO | 90436.273 | 87685.5205 | 85702 | 94791 | 10.61%
19 | 9601000045 | ITEM 19 | 10 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO | 77947.8528 | 80416.9069 | 81375 | 80892 | -0.5935%
20 | NEW | ITEM 20 | 5 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE | NO |  |  |  | 73674
TRANSFORMER CENTRE ON DOUBLE POLE STRUCTURE WITHOUT FENCING
21 | 9601000046 | ITEM 21 | 11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING | No | 92397.6548 | 97321.9996 | 97210 | 96596 | -0.6316%
22 | 9601000047 | ITEM 22 | 11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING | NO | 104788.325 | 104245.6132 | 101077 | 110005 | 8.833%
23 | 9601000009 | ITEM 23 | 11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING | KM | 120622.8672 | 113543.7296 | 113155 | 124985 | 10.45%
24 | 9601000010 | ITEM 24 | 11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING | NO | 174273.3676 | 160525.6246 | 154648 | 176126 | 13.89%
25 | 9601000011 | ITEM 25 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING | NO | 222657.8966 | 196788.929 | 194990 | 219882 | 12.77%
26 | 9602000125 | ITEM 26 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING | NO | 249163.1506 | 227588.454 | 223534 | 252343 | 12.89%
27 | 9602000127 | ITEM 27 | 11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING | NO | 486703.0066 | 469107.3766 | 445569 | 496701 | 11.48%
TRANSFORMER CENTRE ON DOUBLE POLE STRUCTURE WITH FENCING
28 | 9601000046 | ITEM 28 | 11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | No | 115325.0458 | 122487.5476 | 123179 | 123285 | 0.08605%
29 | 9601000047 | ITEM 29 | 11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | NO | 127715.716 | 129411.1612 | 127046 | 136538 | 7.471%
30 | 9601000009 | ITEM 30 | 11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | KM | 148310.1614 | 150730.0108 | 153541 | 151518 | -1.318%
31 | 9601000010 | ITEM 31 | 11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | NO | 197200.7586 | 206384.0562 | 192760 | 202658 | 5.135%
32 | 9601000011 | ITEM 32 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING | NO | 245585.2876 | 255752.9666 | 230022 | 246414 | 7.126%
33 | 9602000125 | ITEM 33 | 11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING | NO | 272090.5416 | 286552.4916 | 258566 | 278876 | 7.855%
34 | 9602000127 | ITEM 34 | 11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING | NO | 509630.3976 | 520261.8648 | 521902 | 523233 | 0.255%
35 |  | ITEM 35 | 11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON 10 MTR PSC POLE WITH FENCING | NO |  |  |  | 506205
36 | 9602000130 | ITEM 36 | 11/0.433 KV 500 KVA DIST. TRANSFORMER CENTRE ON PLINTH | NO | 1612926.651 | 1653639.136 | 1656034 | 2001321 | 20.85%
SPECIAL DESIGNED TRANSFORMER / PAT
37 |  | ITEM 37 | 11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER- SDT - 24 AMP | NO | New | New | 236437 | 243522 | 2.997%
38 |  | ITEM 38 | 11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER - SDT- 30 AMP | NO | New | New | 253004 | 271582 | 7.343%
39 |  | ITEM 39 | 11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 24.7 AMP | NO | New | New | 312016 | 315431 | 1.094%
40 |  | ITEM 40 | 11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 54 AMP | NO | New | New | 432287 | 435702 | 0.79%
LT LINE
41 | 9601000012 | ITEM 41 | L.T. LINE 1 PH 2 WIRE USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 138478.0532 | 158557.0844 | 163563 | 165494 | 1.181%
42 | 9601000013 | ITEM 42 | L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR)WITH WIND PRESSURE 100 KG/M2 | KM | 163452.6132 | 184545.9682 | 191404 | 195120 | 1.941%
43 | 96020002111 | ITEM 43 | L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN - 30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 219148.2808 | 251005.6724 | 258474 | 260755 | 0.8825%
44 | 9601000014 | ITEM 44 | L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING34 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 186576.76 | 208276.5794 | 216994 | 222602 | 2.584%
45 | 9602000212 | ITEM 45 | L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 273634.9708 | 307744.4635 | 317001 | 327010 | 3.157%
46 | 9602000213 | ITEM 46 | L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 9 MTR RSJ POLES 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 671949.0208 | 790673.9519 | 764987 | 838535 | 9.614%
47 | 9602000143 | ITEM 47 | L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 10 MTR PSC POLES 34 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 257243.2556 | 300446.3799 | 304101 | 316875 | 4.201%
48 | 9601000015 | ITEM 48 | L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 224194.911 | 246529.2615 | 258147 | 265142 | 2.71%
49 | 9602000214 | ITEM 49 | L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING PSC POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 284480.8318 | 318365.4876 | 330539 | 336847 | 1.908%
50 | 9602000215 | ITEM 50 | L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING 9 MTR RSJ POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 709628.1718 | 829000.566 | 806243 | 881130 | 9.288%
51 | 9601000016 | ITEM 51 | L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (WEASEL)(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 213809.12 | 236863.8291 | 247501 | 255144 | 3.088%
52 | 9602000216 | ITEM 52 | L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (Span-30 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 272983.7608 | 307340.1626 | 318618 | 325320 | 2.103%
53 | 9602000217 | ITEM 53 | L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING 9 MTR RSJ POLE 34 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2 | KM | 698808.2008 | 818736.8626 | 794949 | 870238 | 9.471%
54 | 9601000017 | ITEM 54 | L.T. LINE 3PHASE 5WIRE FOR AG PURPOSE. VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2 | KM | 250695.271 | 274262.7552 | 287790 | 296751 | 3.114%
55 | 9602000218 | ITEM 55 | L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING RSJ POLE 55 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2 | KM | 735157.2718 | 855299.4567 | 834472 | 911515 | 9.233%
56 | 9602000219 | ITEM 56 | L.T. LINE ADDING OF ONE WIRE IN VERTICAL FORMATION USING55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 | KM | 42179.9734 | 44558.6096 | 47574 | 50395 | 5.93%
SERVICE CONNECTION
57 | 9601000018 | ITEM 57 | SERVICE CONNECTION 3 PHASE 4 WIRE UP TO 5 HP | NO | 6110.2471 | 5926.9891 | 5850 | 6609 | 12.97%
58 | 9601000019 | ITEM 58 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 5 HP TO 10 HP | NO | 6728.5431 | 6554.124 | 6527 | 7236 | 10.86%
59 | 9601000020 | ITEM 59 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 10 HP TO 20 HP | NO | 7392.1011 | 7255.3861 | 7256 | 8076 | 11.3%
60 | 9601000021 | ITEM 60 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 20 HP TO 60 HP | No | 12468.3259 | 13242.9021 | 12957 | 13637 | 5.248%
61 | 9601000022 | ITEM 61 | SERVICE CONNECTION 3 PHASE 4 WIRE FROM 60 HP AND ABOVE | No | 16504.7569 | 16823.7485 | 16615 | 17850 | 7.433%
62 | 9601000023 | ITEM 62 | SINGLE PHASE SERVICE CONNECTION UP TO 6 KW LOAD | No | 2017.468 | 2092.8914 | 2030 | 2720 | 33.99%
63 | 9601000024 | ITEM 63 | SINGLE PHASE STREET LIGHT CONNECTION | No | 2154.5899 | 2245.7269 | 2182 | 2944 | 34.92%
64 | 9601000025 | ITEM 64 | SINGLE PHASE STREET LIGHT FIXTURE | No | 894.5326 | 1035.5282 | 1141 | 1238 | 8.501%
ARIAL BUNCH CABLE
65 | 9601000049 | ITEM 65 | LT LINE 1PH 2 WIRE USING ABC OF SIZE 1x 35 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES | KM | New | 185583.2674 | 192965 | 198577 | 2.908%
66 | 9601000050 | ITEM 66 | LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 35 SQ MM + 1x 16 SQ MM + 1x 25 SQ MM ON 8 MTR PSC POLES | KM | New | 256429.2947 | 264497 | 266739 | 0.8476%
67 |  | ITEM 67 | LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 50 SQ MM + 1x 25 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES | KM |  |  |  | 312493
68 | 9601000051 | ITEM 68 | 11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 8 MTR PSC POLE | KM | New | 648522.6509 | 738088 | 769505 | 4.257%
69 | 9601000052 | ITEM 69 | 11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 11 MTR RSJ POLE | KM | New | 883781.4009 | 975909 | 1083426 | 11.02%
70 |  | ITEM 70 | 11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 10 MTR PSC POLE | KM | New | New | 813387 | 852533 | 4.813%
MISCELLANEOUS
71 |  | ITEM 71 | SINGLE POLE STRUCTURE WITH 11 KV DO FUSE | NO | New | New | 21016 | 21192 | 0.8375%
72 | 9601000048 | ITEM 72 | PROVIDING FANCING AROUND DIST. TRANSFORMER CENTRE | NO | 22927.391 | 25165.548 | 25969 | 26508 | 2.076%
73 |  | ITEM 73 | REPLACEMENT OF SINGLE PHASE SERVICE CONNECTION BY 4.0 MM2 TWIN CORE ARMOURD CABLE | No | New | New | 2457 | 1631 | -33.62%
74 |  | ITEM 74 | REPLACEMENT OF SINGLE PHASE MMB BY SMC | No | New | New | 513 | 331 | -35.48%
75 |  | ITEM 75 | SINGLE PHASE METER REPLACEMENT (UP TO 6 KW LOAD ) | No | New | New | 958 | 619 | -35.39%

## INDEX (hidden)
INDEX
Cost Data & Labour Rates
FY 2019-20
Sr.No. | Sheet | Perticular | Page No
1 | ANNEXTURE-A | ITEM WISE COST DATA ( R E/CITY ) FOR THE YEAR 2019-20
2 | ANNEXTURE-B | COST DATA FOR H.T.POWER SUPPLY FOR YEAR 2019-20.

## 1
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 1
RE/CITY COST DATA FOR THE YEAR 2019-20
TAPPING FROM EXISTING POLES FOR 11 KV LINE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | STRAIGHT CROSS ARMS. (1.15 Mtr) | NO. | 2 | 341 | 682
| 36 11 00 0018 | M.S Angle Tapping-11KV FEBRI. 65x65x6x1150MM | NO. | 2 | 341 | 682
2 |  | BRACING FOR SIDE ARM | NO. | 2 | 224 | 448
| 36 11 00 0031 | Angle Bracing for D.P-65x65x6-750MM | NO. | 2 | 224 | 448
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 1 | 1057 | 1057
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 1 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
4 |  | 11KV PIN INSULATORS WITH SPINDLE | SET | 1 | 219 | 219
| 20 01 00 0006 | (a) 11 KV Pin Insulator | No | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | No | 1 | 0 | 0
219
5 |  | 11KV STRAIN INSULATORS WITH H/W | SET | 3 | 292 | 876
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
6 |  | M.S. BOLTS OF ASSORTED SIZES &
P.G. CLAMPS OR WITH PREFORMED
|  | FITTINGS. |  |  |  | 442
| 15 01 00 0024 | M.S. Bolts & Nuts - 65X16MM | KG | 1.6 | 70 | 112
| 26 01 00 0027/0028 | P.G. Clamp for Weasel/Rabbit | Nos | 3 | 110 | 330
442
7 |  | CLAMP FOR BRACING AND CROSS ARMS | PAIR | 1 | 130 | 130
| 26 01 00 0049 | Side clamp | Nos. | 2 | 65 | 130
8 |  | COST OF MATERIALS |  |  |  | 3854
9 |  | ADD:3% CONTINGENCIES |  |  |  | 115.62
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 77.08
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 77.08
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 578.1
13 |  | A |  |  |  | 4701.88
14 |  | LABOUR CHARGES FOR FIXING
|  | OF CROSS ARMS, BRACING ON LOCATION | NO. | 1 | 313 | 313
15 |  | ERECTION OF STAY SETS. | NO. | 1 | 364 | 364
16 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.15 | 5900 | 885
17 |  | LABOUR CHARGES |  |  |  | 1562
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 234.3
19 |  | B |  |  |  | 1796.3
20 |  | A+B |  |  |  | 6498.18
|  | TOTAL ESTIMATE |  |  | Say Rs. | 6498

## 2
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 2
RE/CITY COST DATA FOR THE YEAR 2019-20
GUARDING UNDER HT AND LT LINE (SPAN-60 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | GUARDING ANGLE CROSS ARM | NO. | 2 | 607 | 1214
| 26 09 00 0029/ 31 | M.S.Angle 65x65x6mm - 2 Mtr for Guarding Angle cross arm/Guarding channel | No | 2 | 607 | 1214
2 |  | BACK CLAMP | NO. | 2 | 65 | 130
| 26 01 00 0049 | Side clamp | No | 2 | 65 | 130
3 | 01 03 00 0003 | G.I. WIRE 10 SWG | KG. | 2 | 70 | 140
4 | 01 03 00 0002 | G.I. WIRE NO. 8 | KG. | 14 | 73 | 1022
5 |  | MISC. ITEMS i.e.BOLTS ,NUTS |  |  |  | 376
WASHER,BINDING WIRES.
| 26 14 00 0012 | Eye-bolt | No | 4 | 74 | 296
| 15 01 00 0024 | Bolts & Nuts - 65x16mm | KG | 0.8 | 70 | 56
| 01 01 00 0003 | Alu.Binding wire | KG | 0.2 | 120 | 24
376
6 |  | COST OF MATERIALS |  |  |  | 2882
7 |  | ADD:3% CONTINGENCIES |  |  |  | 86.46
8 |  | ADD:2% STORAGE CHARGES |  |  |  | 57.64
9 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 57.64
10 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 432.3
11 |  | A |  |  |  | 3516.04
12 |  | LABOUR CHARGES FOR FIXING | NO. | 2 | 313 | 626
OF CROSS ARMS ON LOCATION.
13 |  | PROVIDE GUARDING. | MTR | 60 | 58 | 3480
COMPLETE WITH PAINTING.
14 |  | LABOUR CHARGES |  |  |  | 4106
15 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 615.9
16 |  | B |  |  |  | 4721.9
17 |  | A+B |  |  |  | 8237.94
|  | TOTAL ESTIMATE |  |  | Say Rs. | 8238

## 3
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 3
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 8 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2017 | 4034
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING A.B SWITCH. | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 65 | 260
A B Switch
| 26 01 00 0049 | Side clamp | No | 4 | 65 | 260
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  |  | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 26 01 00 0027/ 0028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 23780.44
|  | ADD:3% CONTINGENCIES |  |  |  | 713.4132
|  | ADD:2% STORAGE CHARGES |  |  |  | 475.6088
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 475.6088
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 3567.066
11 |  | A |  |  |  | 29012.1368
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 246 | 492
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/DO Fuse | SET | 1 | 2067 | 2067
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
18 |  | LABOUR CHARGES |  |  |  | 8623
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1293.45
20 |  | B |  |  |  | 9916.45
21 |  | A+B |  |  |  | 38928.5868
|  | TOTAL ESTIMATE |  |  | Say Rs. | 38929

## 4
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 4
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH ON PSC 10 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10M/ 200 KG | NO. | 2 | 3505 | 7010
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING A.B SWITCH. | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 65 | 260
A B Switch
| 26 01 00 0049 | Side clamp | No | 4 | 65 | 260
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  |  | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 26 01 00 0027/ 0028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 26756.44
|  | ADD:3% CONTINGENCIES |  |  |  | 802.6932
|  | ADD:2% STORAGE CHARGES |  |  |  | 535.1288
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 535.1288
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 4013.466
11 |  | A |  |  |  | 32642.8568
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 400 | 800
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/DO Fuse | SET | 1 | 4030 | 4030
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
18 |  | LABOUR CHARGES |  |  |  | 10894
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1634.1
20 |  | B |  |  |  | 12528.1
21 |  | A+B |  |  |  | 45170.9568
|  | TOTAL ESTIMATE |  |  | Say Rs. | 45171

## 5
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 5
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV DOUBLE POLE STRUCTURE WITH A.B.SWITCH On RSJ 9 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 2 | 10478 | 20956
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING DO Fuse/A.B SWITCH. | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 65 | 1040
| 26 01 00 0049 | Side clamp | No | 16 | 65 | 1040
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  |  | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 26 01 00 0027/ 0028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 41482.44
|  | ADD:3% CONTINGENCIES |  |  |  | 1244.4732
|  | ADD:2% STORAGE CHARGES |  |  |  | 829.6488
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 829.6488
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 6222.366
11 |  | A |  |  |  | 50608.5768
12 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 246 | 492
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON RSJ POLE WITH
|  | AB SWITCH/DO Fuse | SET | 1 | 2485 | 2485
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
ITEM 4
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
17 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
18 |  | LABOUR CHARGES |  |  |  | 17065
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2559.75
20 |  | B |  |  |  | 19624.75
21 |  | A+B |  |  |  | 70233.3268
|  | TOTAL ESTIMATE |  |  | Say Rs. | 70233

## 6
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 6
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV DOUBLE POLE STRUCTURE WITH HG FUSE (WITHOUT AB SWITCH) On PSC 8 MTR POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2017 | 4034
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING DO Fuse | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV DO Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 65 | 130
FOR DO Fuse.
| 26 01 00 0049 | Side clamp | No | 2 | 65 | 130
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 128 | 128
292
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1518.44
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 70 | 364
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 26 01 00 0027/ 0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape for HT Jumpers | Mtr | 20 | 13 | 260
1518.44
10 |  | COST OF MATERIALS |  |  |  | 18060.62
11 |  | ADD:3% CONTINGENCIES |  |  |  | 541.8186
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 361.2124
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 361.2124
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2709.093
15 |  | A |  |  |  | 22033.9564
16 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 246 | 492
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
17 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE,DO Fuse | SET | 1 | 2067 | 2067
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
18 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
19 |  | LABOUR CHARGES |  |  |  | 8623
20 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1293.45
21 |  | B |  |  |  | 9916.45
22 |  | A+B |  |  |  | 31950.4064
|  | TOTAL ESTIMATE |  |  | Say Rs. | 31950

## 7
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 7
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH 34 MM2 AAAC CONDUCTOR( SPAN 50 MTR ) ON 8 MTR PSC POLE WITH WIND PRESSURE ZONE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM Line | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2017 | 40340
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 555 | 11100
3 |  | BACK CLAMP FOR FIXING CROSS ARM. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Sideclamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | HT TOP | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | NO. | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 219 | 13140
| 20 01 00 0006 | (a)11 KV Pin Insulator | No | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | No | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL. | NO. | 12 | 292 | 3504
WITH H/W & PREFORM FITTING.
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 SIZE. | KM. | 3.09 | 19989 | 61766.01
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 3088.2
CLAMP,BINDINGWIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 70 | 812
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.66 | 70 | 1096.2
| 26 01 00 0027 | (c) P.G. Clamp for Weasel | No | 9 | 110 | 990
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 10 | 13 | 130
3088.2
14 |  | COST OF MATERIALS |  |  |  | 148012.21
15 |  | ADD:3% CONTINGENCIES |  |  |  | 4440.3663
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 2960.2442
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2960.2442
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 22201.8315
19 |  | A |  |  |  | 180574.8962
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 246 | 4920
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 757 | 15140
OF PSC POLE INCLUDING DIGGING.
OF PITS FIXING OF POLES FIXTURE
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 364 | 728
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5900 | 1770
28 |  | LABOUR CHARGE |  |  |  | 36032
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 5404.8
30
30 |  | B |  |  |  | 41436.8
31 |  | A+B |  |  |  | 222011.6962
|  | TOTAL ESTIMATE |  |  | Say Rs. | 222012

## 8
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 8
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2017 | 40340
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 555 | 11100
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 219 | 13140
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 12 | 292 | 3504
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 3218.48
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 70 | 812
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.664 | 70 | 1096.48
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 110 | 990
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 20 | 13 | 260
3218.48
14 |  | COST OF MATERIALS |  |  |  | 183056.4
15 |  | ADD:3% CONTINGENCIES |  |  |  | 5491.692
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 3661.128
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3661.128
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 27458.46
19 |  | A |  |  |  | 223328.808
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 246 | 4920
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 757 | 15140
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 364 | 728
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5900 | 1770
28 |  | LABOUR CHARGES |  |  |  | 36032
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 5404.8
30 |  | B |  |  |  | 41436.8
31 |  | A+B |  |  |  | 264765.608
|  | TOTAL ESTIMATE |  |  | Say Rs. | 264766

## 9
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 9
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 8 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 30 | 2017 | 60510
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 555 | 16650
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 219 | 19710
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 292 | 7008
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6131.3
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 19 | 70 | 1330
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 25.99 | 70 | 1819.3
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6131.3
14 |  | COST OF MATERIALS |  |  |  | 230177.22
15 |  | ADD:3% CONTINGENCIES |  |  |  | 6905.3166
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 4603.5444
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4603.5444
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 34526.583
19 |  | A |  |  |  | 280816.2084
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 30 | 246 | 7380
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 757 | 22710
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 364 | 1456
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
28 |  | LABOUR CHARGES |  |  |  | 52750
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7912.5
30
30 |  | B |  |  |  | 60662.5
31 |  | A+B |  |  |  | 341478.7084
|  | TOTAL ESTIMATE |  |  | Say Rs. | 341479

## 10
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 10
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH DOG CONDUCTOR (SPAN-50 MTR) ON PSC POLE (10 MTR) WITH 11 KV MATERIALS
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 20 | 3505 | 70100
2 | 26 09 00 0034 | 11 KV V CROSS ARM. | NO. | 20 | 720 | 14400
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11 KV PIN INSULATOR COMPL. | NO. | 54 | 219 | 11826
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11 KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
456
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
4998
14 |  | COST OF MATERIALS |  |  |  | 308793.42
15 |  | ADD:3% CONTINGENCIES |  |  |  | 9263.8026
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 6175.8684
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 6175.8684
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 46319.013
19 |  | A |  |  |  | 376727.9724
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 246 | 4920
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1815 | 36300
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 364 | 1456
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
28 |  | LABOUR CHARGES |  |  |  | 59690
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 8953.5
30 |  | B |  |  |  | 68643.5
31 |  | A+B |  |  |  | 445371.4724
|  | TOTAL ESTIMATE |  |  | Say Rs. | 445371
5

## 11
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 11
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH DOG CONDUCTOR (SPAN-33 MTR) ON PSC POLE (10 MTR) WITH 11 KV materials
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 30 | 3505 | 105150
2 | 26 09 00 0034 | 11 KV V CROSS ARM. | NO. | 30 | 720 | 21600
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11 KV PIN INSULATOR COMPL. | NO. | 90 | 219 | 19710
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11 KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
456
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
4998
14 |  | COST OF MATERIALS |  |  |  | 367341.42
15 |  | ADD:3% CONTINGENCIES |  |  |  | 11020.2426
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 7346.8284
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7346.8284
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 55101.213
19 |  | A |  |  |  | 448156.5324
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 246 | 7380
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1815 | 54450
|  | OF RSJ POLE INCLUDING DIGGING. |  |  |  |  | 350
|  | OF PITS,FIXING OF POLES FIXTURE, |  |  |  |  | 7000
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
28 |  | LABOUR CHARGES |  |  |  | 85218
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 12782.7
30 |  | B |  |  |  | 98000.7
31 |  | A+B |  |  |  | 546157.2324
|  | TOTAL ESTIMATE |  |  | Say Rs. | 546157
5

## 12
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 12
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH DOG AAAC CONDUCTOR (SPAN-33 MTR) ON RSJ POLE (9 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 30 | 10478 | 314340 | 1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 30 | 12986 | 389580
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 720 | 21600
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950 | 2 | 26 09 00 0034 | 22KV V CROSS ARM. | NO. | 30 | 720 | 21600
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950 | 3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690 |  | 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360 | 4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360 | 5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342 |  | 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
|  | Material required for1 No. Guy set |  |  |  |  | 6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258 |  |  | Material required for1 No. Guy set
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145 |  | 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74 |  | 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365 |  | 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30 |  | 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180 |  | 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5 |  | 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
[6 empty] | 1057 |  | 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860 | [6 empty] | 1057
|  | Material required for 1 No earthing |  |  |  |  | 7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219 |  |  | Material required for 1 No earthing
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43 |  | 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
[6 empty] | 262 |  | 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600 | [6 empty] | 262
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600 | 8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800 |  | 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 219 | 19710
|  | WITH H/W & PREFORM FITTING. |  |  |  |  | 9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
| 20 01 00 0006 | (a11 KV Pin Insulator | NO. | 1 | 219 | 219 | 10 |  | 22KV PIN INSULATOR COMPL. | NO. | 90 | 0 | 0
| 20 10 00 0010 | (b)11 KV GI Pin | NO. | 1 | 0 | 0 |  |  | WITH H/W & PREFORM FITTING.
[6 empty] | 219 |  | 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 1 | 0 | 0
11 |  | 11KV STRAIN INSULATOR COMPL. | [5 empty] | 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 1 | 0 | 0
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944 | [6 empty] | 0
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328 | 11 |  | 22KV STRAIN INSULATOR COMPL.
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128 |  |  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944
456
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42 |  | 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998 |  | 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
|  | CLAMP;BINDING WIRE,TAPS,BOLT, | [10 empty] | 456
|  | NUTS WITH PREFORM FITTING. |  |  |  |  | 12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0 | 13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640 |  |  | CLAMP;BINDING WIRE,TAPS,BOLT,
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108 |  |  | NUTS WITH PREFORM FITTING.
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234 |  | 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
[6 empty] | 4998 |  | 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
14 |  | COST OF MATERIALS |  |  |  | 576531.42 |  | 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
15 |  | ADD:3% CONTINGENCIES |  |  |  | 17295.9426 |  | 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 11530.6284 |  | 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11530.6284 | [6 empty] | 4998
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 86479.713
19 |  | A |  |  |  | 703368.3324 | 14 |  | COST OF MATERIALS |  |  |  | 632061.42
[7 empty] | 19 |  | A |  |  |  | 632061.42
[9 empty] | ADD:3% CONTINGENCIES |  |  |  | 18961.8426
[9 empty] | ADD:2% STORAGE CHARGES |  |  |  | 12641.2284
[9 empty] | ADD:2% TRANSPORTATION & MISC. |  |  |  | 12641.2284
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400 |  |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 94809.213
21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 246 | 7380
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575 |  |  | Total ….A |  |  |  | 771114.9324
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1268 | 38040
|  | OF RSJ POLE INCLUDING DIGGING. |  |  |  |  | 20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
|  | OF PITS,FIXING OF POLES FIXTURE, |  |  |  |  | 21 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 230 | 6900
|  | INSULATOR & PAINTING STEEL POLE |  |  |  |  | 22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 3162 | 9486 | 23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1180 | 35400
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 364 | 1456 |  |  | OF RSJ POLE INCLUDING DIGGING.
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570 |  |  | OF PITS,FIXING OF POLES FIXTURE,
|  | EARTHING WITH SALT & COAL. |  |  |  |  | 24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 2900 | 8700
27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5900 | 125670
28 |  | LABOUR CHARGES |  |  |  | 195577 | 25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 335 | 2010
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 29336.55
[7 empty] | 26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 370 | 11100
30 |  | B |  |  |  | 224913.55 | 27 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5900 | 125670
31 |  | A+B |  |  |  | 928281.8824
|  | TOTAL ESTIMATE |  |  | Say Rs. | 928282 | 28 |  | LABOUR CHARGES |  |  |  | 190755
[7 empty] | 29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 28613.25
30
[7 empty] | 31 |  | B |  |  |  | 219368.25
[7 empty] | 32 |  | Sub Total(A+B) |  |  |  | 990483.1824
[9 empty] | Total Estimate |  |  | Say Rs. | 990483.1824

## 13
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 13
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-50 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 20 | 3505 | 70100
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 555 | 11100
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 219 | 13140
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 12 | 292 | 3504
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 3088.48
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 70 | 812
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.664 | 70 | 1096.48
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 110 | 990
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 10 | 13 | 130
3088.48
14 |  | COST OF MATERIALS |  |  |  | 212686.4
15 |  | ADD:3% CONTINGENCIES |  |  |  | 6380.592
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 4253.728
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4253.728
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 31902.96
19 |  | A |  |  |  | 259477.408
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 400 | 8000
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1815 | 36300
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 364 | 728
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5900 | 1770
28 |  | LABOUR CHARGES |  |  |  | 60272
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9040.8
30 |  | B |  |  |  | 69312.8
31 |  | A+B |  |  |  | 328790.208
|  | TOTAL ESTIMATE |  |  | Say Rs. | 328790

## 14
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 14
RE/CITY COST DATA FOR THE YEAR 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR (SPAN-33 MTR) ON 10 MTR PSC POLE WITH WIND PRESSURE 100 KG/M2 WITH 11 KV MATERIALS
SR | ITEM CODE NO. | PARTICULARS for 1 KM HT LINE | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 30 | 3505 | 105150
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 555 | 16650
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0069 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 219 | 19710
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 292 | 7008
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 3088.48
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 70 | 812
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.664 | 70 | 1096.48
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 110 | 990
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.5 | 120 | 60
| 19 05 00 0006 | (e) HT Tape | Mtr | 10 | 13 | 130
3088.48
14 |  | COST OF MATERIALS |  |  |  | 271774.4
15 |  | ADD:3% CONTINGENCIES |  |  |  | 8153.232
16 |  | ADD:2% STORAGE CHARGES |  |  |  | 5435.488
17 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5435.488
18 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 40766.16
19 |  | A |  |  |  | 331564.768
20 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
21 |  | CARTING OF PSC POLES AT DESTI. | NO. | 30 | 400 | 12000
22 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
23 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1815 | 54450
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
24 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
25 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 364 | 1456
26 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT & COAL.
27 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5900 | 1770
28 |  | LABOUR CHARGES |  |  |  | 87340
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 13101
30
30 |  | B |  |  |  | 100441
31 |  | A+B |  |  |  | 432005.768
|  | TOTAL ESTIMATE |  |  | Say Rs. | 432006

## 15
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 15
RE/CITY COST DATA FOR THE YEAR 2019-20
UNDER GROUND RAILWAY CROSSING (DOUBLE TRACK- BROAD GAUGE) FOR 11 KV SYSTEM
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 36 04 00 0001 | RSJ 116*100 MM 9 MTR. | NO. | 4 | 10478 | 41912
2 | 26 09 00 0034 | V CROSS ARMS 11KV | NO. | 4 | 555 | 2220
3 |  | STRAIN INSULATOR 11 KV WITH H/W | SET | 6 | 292 | 1752
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
4 | 04 05 00 0009 | 11 KVXLPE CABLE 3 CORE 185 mm2 SIZE.(Double CKT) | MTR | 230 | 1034 | 237820
5 |  | ANTI-CLIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | No | 2 | 120 | 240
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
8 |  | SUNDRY MATERIAL SUCH AS |  |  |  | 1498
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6.4 | 70 | 448
| 19 05 00 0006 | (b) HT Binding Tape | Mtr | 30 | 13 | 390
| 26 01 00 0027/0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
1498
9 |  | COST OF MATERIALS |  |  |  | 291904
10 |  | ADD:3% CONTINGENCIES |  |  |  | 8757.12
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 5838.08
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5838.08
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 43785.6
14 |  | A |  |  |  | 356122.88
15 |  | LABOUR CHARGES FOR COMPLETE |  |  | ----LS---- | 350000
WORK OF CROSSING
(INCLUDING LAYING, JOINTING, INSERTATIOIN OF 150MM DIA C. I. PIPE UNDER RAILWAY TRACK USING HORIZONTAL AUGER GUIDED BORING BY PUSH THROUGH METHOD; INSERTATION OF C. I. PIPE IN SIDE RAILWAY BOUNDRY BY CUT AND FILL METHOD; PROVIDING AND SUPPLY OF 150MM DIA C. I. PIPE; LAYING OF 11KV XLPE CABLE IN SIDE C. I. PIPE; PROVIDING SUPPLY AND FIXING 185MM2 CABLE BOX, TERMINATION KIT; PROVIDING PAINTING, FABRICATION AND FIXING OF CABLE MARKER; PROVIDING AND FIXING OF G. I, PIPE ON ERECTED STRUCTURE FOR MECHANICAL PROTECTION OF XLPE CABLE & PROVIDING EARTHING AS PER RAILWAY AUTHORITY ETC.) THE FOLLOWING ITEMS ARE COVERED IN THE SCOPE OF SUPPLIER/CONTRACTOR. LENGTH OF CI PIPE, EARTHING, ITS INSTALLATION EVERYTHING BETWEEN TWO END TERMINATION ACROSS THE RAILWAY TRACK SHALL BE ACCORDING TO DRAWING APPROVED BY CONCERN RAILWAY AUTHORITY. CABLE WILL BE CARTED FROM STORE TO SITE BY CONTRACTOR. ONLY CABLE WILL BE PROVIDED BY UGVCL.
16 |  | CARTING OF RSJ POLE AT DEST. | NO. | 2 | 246 | 492
17 |  | CARTING OF LINE MATERIAL AT |  |  | ----LS---- | 575
WORK SITE
18 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 2.26 | 5900 | 13334
19 |  | LABOUR CHARGES |  |  |  | 364401
20 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 54660.15
21
21 |  | B |  |  |  | 419061.15
22 |  | A+B |  |  |  | 775184.03
|  | TOTAL ESTIMATE |  |  | Say Rs. | 775184

## 16
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 16
RE/CITY COST DATA FOR THE YEAR 2019-20
RIVER CROSSING (11KV) on 10 MTR PSC POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 Meter 200 KG | NO. | 4 | 3505 | 14020
2 |  | TOP CROSS ARMS FOR TERMINATING | NO. | 4 | 834 | 3336
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750 mm for top cross arm for terminating line | No | 4 | 834 | 3336
3 |  | BRACING FOR DOUBLE POLE STRUCTURE | SET | 2 | 3336 | 6672
|  | ( 4 angles per set) |  | 8 | 834 | 6672
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV
4 |  | 11 KV STRAIN INSULATOR H/W WITH | SET | 12 | 292 | 3504
PREFORMED FITTING
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 1 | 128 | 128
292
5 |  | ANTI-CLIMBING DEVICES. | NO. | 4 | 120 | 480
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 4 | 120 | 480
30.192
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 4 | 60 | 240
7 |  | EARTHING OF D.P. STRUCTURE | NO. | 4 | 438 | 1752
Material required for 1 No. Pipe Type earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 1 Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (e) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (f) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | GUY SET WITH PREFORMED FITTING | NO. | 8 | 1057 | 8456
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
9 |  | SUNDRY MATERIAL SUCH AS BOLT & |  |  |  | 1498.6
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 70 | 336
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 4.98 | 70 | 348.6
| 26 01 00 0027/ 0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 19 05 00 0006 | (d) HT Tape for binding | Mtr | 10 | 13 | 130
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.2 | 120 | 24
1498.6
10 |  | COST OF MATERIALS |  |  |  | 39958.6
11 |  | ADD:3% CONTINGENCIES |  |  |  | 1198.758
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 799.172
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 799.172
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 5993.79
15 |  | A |  |  |  | 48749.492
16 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE . | NO. | 2 | 4030 | 8060
17 |  | INSTALLATION OF EARTHING COIL | NO. | 4 | 419 | 1676
PLATE TYPE WITH SALT &COAL
ITEM 14
18 |  | PROVIDING GUY SET COMP.WITH | NO. | 8 | 364 | 2912
ALL ACCESSORES &FITTING
19 |  | CARTING OF POLE AT DEST. | NO. | 4 | 400 | 1600
20 |  | CARTING OF MATERIAL AT WORK SITE |  |  | ----LS---- | 575
21 |  | CONCRETING OF GUY & PSC POLES WITH MATERIAL(1:2:4) | CMT | 1.2 | 5900 | 7080
22 |  | LABOUR CHARGES.. |  |  |  | 21903
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3285.45
24 |  | B |  |  |  | 25188.45
25 |  | A+B |  |  |  | 73937.942
|  | TOTAL ESTIMATE |  |  | Say Rs. | 73938

## 17
UTTAR GUJARAT VIJ COMPANY LIMITED | [5 empty] | COST DATA
ITEM 17
RE/CITY COST DATA FOR THE YEAR 2019-20
25 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2017 | 2017
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 2864
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 81 | 81
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 719 | 719
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 533 | 1066
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 185 | 370
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing DO Fuse | No | 1 | 428 | 428
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing DO Fuse. | No | 2 | 100 | 200
2864
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 1 | 6900 | 6900
10 |  | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 5 | 61.304 | 306.52
11 |  | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV.(Amorphos) | NO. | 1 | 55350 | 55350
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 985.21
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 70 | 420
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 70 | 99.4
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 65 | 390
985.21
15 |  | COST OF MATERIALS |  |  |  | 79644.03
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2389.3209
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1592.8806
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1592.8806
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 11946.6045
20 |  | A |  |  |  | 97165.7166
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,DO FuseS,
|  | DIST.BOX ETC. | NO. | 1 | 2949 | 2949
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 364 | 728
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 246 | 246
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5900 | 4307
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
28 |  | LABOUR CHARGES |  |  |  | 10612
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1591.8
31 |  | B |  |  |  | 12203.8
32 |  | A+B |  |  |  | 109369.5166
|  | TOTAL ESTIMATE |  |  | Say Rs. | 109370
S

## 18
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 18
RE/CITY COST DATA FOR THE YEAR 2019-20
16 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2017 | 2017
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 2864
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 81 | 81
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 719 | 719
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 533 | 1066
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 185 | 370
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing DO Fuse | No | 1 | 428 | 428
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing DO Fuse. | No | 2 | 100 | 200
2864
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 1 | 6900 | 6900
10 |  | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 5 | 61.304 | 306.52
11 |  | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 16 KVA 11KV/0.433KV. | NO. | 1 | 43400 | 43400
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 985.21
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 70 | 420
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 70 | 99.4
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 65 | 390
985.21
15 |  | COST OF MATERIALS |  |  |  | 67694.03
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2030.8209
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1353.8806
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1353.8806
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 10154.1045
20 |  | A |  |  |  | 82586.7166
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 2949 | 2949
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 364 | 728
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 246 | 246
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5900 | 4307
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
28 |  | LABOUR CHARGES |  |  |  | 10612
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1591.8
30 |  | B |  |  |  | 12203.8
31 |  | A+B |  |  |  | 94790.5166
|  | TOTAL ESTIMATE |  |  | Say Rs. | 94791

## 19
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 19
RE/CITY COST DATA FOR THE YEAR 2019-20
10 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2017 | 2017
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 2864
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 81 | 81
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 719 | 719
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 533 | 1066
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 185 | 370
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing HG Fuse | No | 1 | 428 | 428
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing HG Fuse. | No | 2 | 100 | 200
2864
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 1 | 6900 | 6900
10 |  | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 5 | 61.304 | 306.52
11 |  | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
| 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV. | NO. | 1 | 32008 | 32008
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 985.21
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 70 | 420
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 70 | 99.4
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 65 | 390
985.21
15 |  | COST OF MATERIALS |  |  |  | 56302.03
16 |  | ADD:3% CONTINGENCIES |  |  |  | 1689.0609
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1126.0406
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1126.0406
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8445.3045
20 |  | A |  |  |  | 68688.4766
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 2949 | 2949
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 364 | 728
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 246 | 246
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5900 | 4307
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES |  |  |  | 10612
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1591.8
30 |  | B |  |  |  | 12203.8
31 |  | A+B |  |  |  | 80892.2766
|  | TOTAL ESTIMATE |  |  | Say Rs. | 80892

## 20
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 20
RE/CITY COST DATA FOR THE YEAR 2019-20
5 KVA CAPACITY 11 KV/0.433 KV TRANSFORMER CENTRE USING SINGLE POLE STRUCTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 1 | 2017 | 2017
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 2864
OF 11KV FUSES .
| 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | No | 1 | 81 | 81
| 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 719 | 719
| 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | No | 2 | 533 | 1066
| 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | No | 2 | 185 | 370
| 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing HG Fuse | No | 1 | 428 | 428
| 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing HG Fuse. | No | 2 | 100 | 200
2864
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 2 | 846.06 | 1692.12
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 2 | 309 | 618
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NATURAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 1 | 120 | 120
| 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 1 | 120 | 120
9 | 21 04 00 0002 |  |  |  | 6900 | 0
10 |  | PVC INSULATED & SHEATHED 4 MM2 | MTR | 5 | 9.35 | 46.75
2 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0035 | 2C * 4mm2 LT PVC Cable | MTR | 5 | 9.35 | 46.75
11 |  | -DO- 4 MM2 OUT GOING SIDE. | MTR | 30 | 9.35 | 280.5
| 04 01 00 0035 | 2 C x 4mm2 LT PVC Cable | MTR | 30 | 9.35 | 280.5
12 | 44 06 02 0002 | X'MER 5 KVA | NO. | 1 | 37400 | 37400
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 814 | 814
| 1601000073 | (i) 5-30 A Static Meter | NO | 1 | 465 | 465
| 1607000009 | (ii) 1-ph SMB | NO | 1 | 219 | 219
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
814
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 985.21
CLAMPS,ZYKON BOLTS-6 NOS & NUTS ETC.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6 | 70 | 420
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 1.42 | 70 | 99.4
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 16 00 0005 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 15 00 0020 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h)Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 01 00 0049 | (i) Side Clamp | NO. | 6 | 65 | 390
985.21
15 |  | COST OF MATERIALS |  |  |  | 50385.58
16 |  | ADD:3% CONTINGENCIES |  |  |  | 1511.5674
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1007.7116
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1007.7116
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 7557.837
20 |  | A |  |  |  | 61470.4076
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 2949 | 2949
EXCLUDING GUY AND EARTHING
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 2 | 364 | 728
24 |  | CARTING OF POLE AT WORK SITE | NO. | 1 | 246 | 246
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.73 | 5900 | 4307
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES |  |  |  | 10612
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1591.8
30 |  | B |  |  |  | 12203.8
31 |  | A+B |  |  |  | 73674.2076
|  | TOTAL ESTIMATE |  |  | Say Rs. | 73674

## 21
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 21
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 7032
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 224 | 896
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7032
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 6900 | 6900
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV.(LEVEL 2) | NO. | 1 | 32008 | 32008
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 2581.31
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 70 | 389.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2581.31
15 |  | COST OF MATERIALS |  |  |  | 66197.13
16 |  | ADD:3% CONTINGENCIES |  |  |  | 1985.9139
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1323.9426
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1323.9426
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 9929.5695
20 |  | A |  |  |  | 80760.4986
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 13770
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2065.5
30 |  | B |  |  |  | 15835.5
31 |  | A+B |  |  |  | 96595.9986
|  | TOTAL ESTIMATE |  |  | Say Rs. | 96596

## 22
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 22
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 7032
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 224 | 896
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7032
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 6900 | 6900
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0008 | X'MER 16 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 43400 | 43400
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 2581.31
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 70 | 389.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/ 0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2581.31
15 |  | COST OF MATERIALS |  |  |  | 77589.13
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2327.6739
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1551.7826
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1551.7826
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 11638.3695
20 |  | A |  |  |  | 94658.7386
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 350
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 350
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 13345
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2001.75
30 |  | B |  |  |  | 15346.75
31 |  | A+B |  |  |  | 110005.4886
|  | TOTAL ESTIMATE |  |  | Say Rs. | 110005

## 23
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 23
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 7100
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7100
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 6900 | 6900
10 | 04 01 00 0035 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0035 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 55350 | 55350
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 2441.31
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/ 0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2441.31
15 |  | COST OF MATERIALS |  |  |  | 89467.13
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2684.0139
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1789.3426
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1789.3426
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 13420.0695
20 |  | A |  |  |  | 109149.8986
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 13770
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2065.5
30 |  | B |  |  |  | 15835.5
31 |  | A+B |  |  |  | 124985.3986
|  | TOTAL ESTIMATE |  |  | Say Rs. | 124985

## 24
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 24
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 7100
OF FUSES 11KV.
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7100
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 438 | 1314
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | 63KVA L.T. DIST. BOX | NO. | 1 | 6993 | 6993
10 |  | PVC INSULATED & SHEATHED 70 MM2 | MTR | 5 | 184.08 | 920.4
| 04 01 00 0004 | 3.5 Cx 70mm2 LT PVC Cable | MTR | 5 | 184.08 | 920.4
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 30 | 82.83 | 2484.9
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 30 | 82.83 | 2484.9
12 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV.LEVEL-2) | NO. | 1 | 95000 | 95000
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2981 | 2981
| 1601000069 | (i) 100/5 A Static Meter . | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000046 | (iv) Ring Type LT CT-100/5 A | SET | 1 | 735 | 735
2981
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2505.18
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/0028 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 14 | 42
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 3.54 | 7.08
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 3.2 | 19.2
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 2.7 | 5.4
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2505.18
15 |  | COST OF MATERIALS |  |  |  | 131385.66
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3941.5698
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2627.7132
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2627.7132
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 19707.849
20 |  | A |  |  |  | 160290.5052
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 13770
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2065.5
30
30 |  | B |  |  |  | 15835.5
31 |  | A+B |  |  |  | 176126.0052
|  | TOTAL ESTIMATE |  |  | Say Rs. | 176126

## 25
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 25
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 8563 | 8563
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 137.82 | 4134.6
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 137.82 | 4134.6
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 124200 | 124200
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2616.4
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/ 0028 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 3.2 | 9.6
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 65 | 780
2616.4
15 |  | COST OF MATERIALS |  |  |  | 167251.38
16 |  | ADD:3% CONTINGENCIES |  |  |  | 5017.5414
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 3345.0276
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3345.0276
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 25087.707
20 |  | A |  |  |  | 204046.6836
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 13770
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2065.5
30 |  | B |  |  |  | 15835.5
31 |  | A+B |  |  |  | 219882.1836
|  | TOTAL ESTIMATE |  |  | Say Rs. | 219882

## 26
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 26
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 10478 | 20956
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 8563 | 8563
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 137.82 | 4134.6
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 137.82 | 4134.6
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. (LEVEL-2) | NO. | 1 | 124200 | 124200
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3796.7
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 70 | 700
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 3.2 | 6.4
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 65 | 1560
3796.7
15 |  | COST OF MATERIALS |  |  |  | 185353.68
16 |  | ADD:3% CONTINGENCIES |  |  |  | 5560.6104
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 3707.0736
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3707.0736
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 27803.052
20 |  | A |  |  |  | 226131.4896
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
28 |  | LABOUR CHARGES… |  |  |  | 22793
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3418.95
30 |  | B |  |  |  | 26211.95
31 |  | A+B |  |  |  | 252343.4396
|  | TOTAL ESTIMATE |  |  | Say Rs. | 252343

## 27
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 27
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITHOUT FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 10478 | 20956
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 200 KVA L.T. DIST. BOX | NO. | 1 | 82156 | 82156
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 70 MM2 OUT GOING SIDE. | MTR | 30 | 184.08 | 5522.4
| 04 01 00 0003 | 3.5 C x 70mm2 LT PVC Cable | MTR | 30 | 184.08 | 5522.4
12 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 249500 | 249500
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3808.7
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 70 | 700
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-20 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 3.2 | 6.4
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 65 | 1560
3808.7
15 |  | COST OF MATERIALS |  |  |  | 385646.48
16 |  | ADD:3% CONTINGENCIES |  |  |  | 11569.3944
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 7712.9296
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7712.9296
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 57846.972
20 |  | A |  |  |  | 470488.7056
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
28 |  | LABOUR CHARGES… |  |  |  | 22793
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3418.95
30 |  | B |  |  |  | 26211.95
31 |  | A+B |  |  |  | 496700.6556
|  | TOTAL ESTIMATE |  |  | Say Rs. | 496701

## 28
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 28
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 10 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 7032
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 224 | 896
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7032
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 6900 | 6900
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV. | NO. | 1 | 32008 | 32008
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 2581.31
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 70 | 389.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2581.31
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 80748.89
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2422.4667
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1614.9778
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1614.9778
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 12112.3335
20 |  | A |  |  |  | 98513.6458
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.28314 | 5900 | 1670.5077
28 |  | LABOUR CHARGES… |  |  |  | 21540.5077
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3231.0762
30 |  | B |  |  |  | 24771.5839
31 |  | A+B |  |  |  | 123285.2297
|  | TOTAL ESTIMATE |  |  | Say Rs. | 123285

## 29
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 29
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 16 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 7032
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 224 | 896
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7032
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 6900 | 6900
10 | 04 01 00 0055 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0055 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0008 | X'MER 16 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 43400 | 43400
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000008 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 2581.31
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 220x16mm | KG | 5.56 | 70 | 389.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2581.31
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 92140.89
16 |  | ADD:3% CONTINGENCIES |  |  |  | 2764.2267
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 1842.8178
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1842.8178
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 13821.1335
20 |  | A |  |  |  | 112411.8858
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 350
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 350
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 20979
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3146.85
30 |  | B |  |  |  | 24125.85
31 |  | A+B |  |  |  | 136537.7358
|  | TOTAL ESTIMATE |  |  | Say Rs. | 136538

## 30
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 30
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 25 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STEEL STRUCTURE FOR TERMINATING
|  | LINES MOUNTING OF TRANS./FIXING | L.S |  |  | 7100
OF 11KV FUSES .
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 11 00 0024 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7100
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 .848 - Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (c) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0002 | L.T. DIST. BOX FOR 25 KVA X-MER | NO. | 1 | 6900 | 6900
10 | 04 01 00 0035 | PVC INSULATED & SHEATHED 16 MM2 | MTR | 5 | 61.304 | 306.52
4 CORE CABLE FOR INCOMING SIDE.
11 | 04 01 00 0035 | -DO- BUT 16 MM2 OUT GOING SIDE. | MTR | 30 | 61.304 | 1839.12
12 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 55350 | 55350
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2129 | 2129
| 1601000073 | (i) 10-60 A Static Meter | NO | 1 | 1472 | 1472
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
2129
14 |  | SUNDRY MATERIALS SUCH AS PG |  |  |  | 2441.31
CLAMPS, BOLTS & NUTS ETC.
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0004 | (c) Fuse element-3 Amp | NO. | 3 | 14 | 42
| 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 04 15 00 0021 | (e) Alu.lugs -Trans. LT 16 SQ.MM Cable | NO. | 6 | 2.7 | 16.2
| 04 15 00 0020 | (f) Alu.lugs -Trans. LT 10 SQ.MM Cable | NO. | 2 | 1.77 | 3.54
| 04 16 00 0005 | (g) Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 3 | 2.7 | 8.1
| 04 16 00 0004 | (h) Alu.lugs for kit-Kat 10 SQ.MM Cable | NO. | 1 | 1.77 | 1.77
| 26 13 00 0002 | (i) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2441.31
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 104018.89
16 |  | ADD:3% CONTINGENCIES |  |  |  | 3120.5667
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2080.3778
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2080.3778
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 15602.8335
20 |  | A |  |  |  | 126903.0458
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 21404
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3210.6
30 |  | B |  |  |  | 24614.6
31 |  | A+B |  |  |  | 151517.6458
|  | TOTAL ESTIMATE |  |  | Say Rs. | 151518

## 31
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 31
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 63 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 7100
OF FUSES 11KV.
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 6 | 834 | 5004
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
7100
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 438 | 1314
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | 63KVA L.T. DIST. BOX | NO. | 1 | 6993 | 6993
10 |  | PVC INSULATED & SHEATHED 70 MM2 | MTR | 5 | 184.08 | 920.4
| 04 01 00 0004 | 3.5 Cx 70mm2 LT PVC Cable | MTR | 5 | 184.08 | 920.4
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 30 | 82.83 | 2484.9
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 30 | 82.83 | 2484.9
12 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 95000 | 95000
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2981 | 2981
| 1601000069 | (i) 100/5 A Static Meter . | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph MMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000046 | (iv) Ring Type LT CT-100/5 A | SET | 1 | 735 | 735
2981
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2505.18
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 14 | 42
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 3.54 | 7.08
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 3.2 | 19.2
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 2.7 | 5.4
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2505.18
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 145937.42
16 |  | ADD:3% CONTINGENCIES |  |  |  | 4378.1226
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 2918.7484
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2918.7484
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 21890.613
20 |  | A |  |  |  | 178043.6524
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (LumSum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 21404
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3210.6
30 |  | B |  |  |  | 24614.6
31 |  | A+B |  |  |  | 202658.2524
|  | TOTAL ESTIMATE |  |  | Say Rs. | 202658

## 32
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 32
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE USING DOUBLE POLE STRUCTURE ON 8 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 8563 | 8563
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 137.82 | 4134.6
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 137.82 | 4134.6
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 124200 | 124200
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2616.4
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 3.2 | 9.6
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 65 | 780
2616.4
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 181803.14
16 |  | ADD:3% CONTINGENCIES |  |  |  | 5454.0942
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 3636.0628
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3636.0628
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 27270.471
20 |  | A |  |  |  | 221799.8308
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 21404
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3210.6
30 |  | B |  |  |  | 24614.6
31 |  | A+B |  |  |  | 246414.4308
|  | TOTAL ESTIMATE |  |  | Say Rs. | 246414

## 33
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 33
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 100 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 10478 | 20956
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 100 KVA L.T. DIST. BOX | NO. | 1 | 8563 | 8563
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 50 MM2 OUT GOING SIDE. | MTR | 30 | 137.82 | 4134.6
| 04 01 00 0003 | 3.5 C x 50mm2 LT PVC Cable | MTR | 30 | 137.82 | 4134.6
12 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 124200 | 124200
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3796.7
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 70 | 700
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 3.2 | 6.4
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 65 | 1560
3796.7
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 199905.44
16 |  | ADD:3% CONTINGENCIES |  |  |  | 5997.1632
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 3998.1088
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3998.1088
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 29985.816
20 |  | A |  |  |  | 243884.6368
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 30427
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 4564.05
30 |  | B |  |  |  | 34991.05
31 |  | A+B |  |  |  | 278875.6868
|  | TOTAL ESTIMATE |  |  | Say Rs. | 278876

## 34
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 34
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON RSJ POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 10478 | 20956
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 200 KVA L.T. DIST. BOX | NO. | 1 | 82156 | 82156
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 70 MM2 OUT GOING SIDE. | MTR | 30 | 184.08 | 5522.4
| 04 01 00 0003 | 3.5 C x 70mm2 LT PVC Cable | MTR | 30 | 184.08 | 5522.4
12 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 249500 | 249500
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3808.7
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 70 | 700
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-20 Amp | No | 3 | 18 | 54
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 3.2 | 6.4
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 65 | 1560
3808.7
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 400198.24
16 |  | ADD:3% CONTINGENCIES |  |  |  | 12005.9472
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 8003.9648
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 8003.9648
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 60029.736
20 |  | A |  |  |  | 488241.8528
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 30427
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 4564.05
30 |  | B |  |  |  | 34991.05
31 |  | A+B |  |  |  | 523232.9028
|  | TOTAL ESTIMATE |  |  | Say Rs. | 523233

## 35
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 33
RE/CITY COST DATA FOR THE YEAR 2019-20 |  |  |  |  | COST DATA
11/0.433 KV 200 KVA DIST. TRANSFORMER CENTRE ON 10 MTR PSC POLE WITH FENCING
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 2 | 3505 | 7010
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING |  |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
9 | 21 04 00 0009 | 200 KVA L.T. DIST. BOX | NO. | 1 | 82156 | 82156
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 5 | 363.44 | 1817.2
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 5 | 363.44 | 1817.2
11 |  | -DO- BUT 70 MM2 OUT GOING SIDE. | MTR | 30 | 184.08 | 5522.4
| 04 01 00 0003 | 3.5 C x 70mm2 LT PVC Cable | MTR | 30 | 184.08 | 5522.4
12 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV.(LEVEL-2) | NO. | 1 | 249500 | 249500
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 2635 | 2635
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
| 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 1 | 389 | 389
2635
14 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3796.7
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 10 | 70 | 700
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 3.2 | 6.4
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 24 | 65 | 1560
3796.7
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995
14551.76
15 |  | COST OF MATERIALS |  |  |  | 386240.24
16 |  | ADD:3% CONTINGENCIES |  |  |  | 11587.2072
17 |  | ADD:2% STORAGE CHARGES |  |  |  | 7724.8048
18 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7724.8048
19 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 57936.036
20 |  | A |  |  |  | 471213.0928
21 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6900 | 6900
22 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
23 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
24 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 246 | 492
25 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
26 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
27 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534
28 |  | LABOUR CHARGES… |  |  |  | 30428
29 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 4564.2
30 |  | B |  |  |  | 34992.2
31 |  | A+B |  |  |  | 506205.2928
|  | TOTAL ESTIMATE |  |  | Say Rs. | 506205

## 36
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 36
RE/CITY COST DATA FOR THE YEAR 2019-20 |  |  |  |  | COST DATA
11/0.433 KV 500 KVA DIST. TRANSFORMER CENTRE ON PLINTH
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 2 | 10478 | 20956 | 18464
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 6208 | 5674
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 2750 mm | NO | 2 | 1287 | 2574 | 2380
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 834 | 1668 | 1512
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668 | 1512
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 0 | 241 | 0 | 0
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298 | 270
[6 empty] | 6208 | 5674
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18 | 2961
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927 | 1017
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228 | 3916.2
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258 | 245
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145 | 137
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74 | 71
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365 | 319.05
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30 | 28
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180 | 174
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5 | 5
[6 empty] | 1057 | 979.05
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120 | 120
7 |  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314 | 1313.82
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313 | 281.24
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43 | 90
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73 | 58.2
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9 | 8.5
[6 empty] | 438 | 437.94
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240 | 200
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240 | 200
9 | 21 04 00 0009 | 500 KVA L.T. DIST. BOX | NO. | 1 | 183748 | 183748 | 167990 | 15758 | 9.3803
10 |  | PVC INSULATED & SHEATHED 150 MM2 | MTR | 15 | 363.44 | 5451.6 | 5185.5
3.5 CORE CABLE FOR INCOMING SIDE.
| 04 01 00 0007 | 3.5 C x 150mm2 LT PVC Cable | MTR | 15 | 363.44 | 5451.6 | 5185.5
11 |  | -DO- BUT 150 MM2 OUT GOING SIDE. | MTR | 45 | 363.44 | 16354.8 | 15556.5
| 04 01 00 0003 | 3.5 C x 150 mm2 LT PVC Cable | MTR | 45 | 363.44 | 16354.8 | 15556.5
12 | 44 06 02 0023 | X'MER 500 KVA 11KV/0.433KV. | NO. | 1 | 849000 | 849000 | 581066 | 267934 | 46.1108
13 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 2 | 2806 | 5612 | 9652
| 1601000070 | (i) 200/5 A Static Meter. | NO | 1 | 1589 | 1589 | 2162
| 1607000009 | (ii) 3-ph SMB | NO | 1 | 527 | 527 | 583
| 2601000061 | (iii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130 | 126
| 1608000049 | (iv) Ring Type LT CT-900/5A | SET | 1 | 560 | 560 | 1955
[6 empty] | 2806 | 4826
14 | 614000011 | 11 KV R M U(SF-6) | NO | 1 | 435115 | 435115 | 400000
15 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 3436.7 | 3126.05
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 8.4 | 70 | 588 | 630
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2 | 267
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3 | 231.75
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660 | 420
| 13 02 00 0006 | (e) Fuse element-20 Amp | No | 3 | 18 | 54 | 48
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6 | 10.8
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4 | 7.2
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111 | 87
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8 | 10.2
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 6 | 5.5 | 33 | 27.6
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 2 | 3.2 | 6.4 | 6.5
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180 | 120
| 26 01 00 0049 | (m) Side Clamp | NO. | 20 | 65 | 1300 | 1260
[6 empty] | 3436.7 | 3126.05
|  | PROVIDING FANCING AROUND TRANSFORMER CENTRE |  |  |  | 14551.76 | 13961.4
| 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 49.5 mm X 49.5 mm X 4.5 mm with conversion factor of 5.95 mtr/Kg | KG. | 62.48 | 54 | 3373.92 | 4694.4
|  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 mtr/Kg | KG. | 117.18 | 50 | 5859 | 5460
|  | M.S.Angle 25x25x3mm with conversion factor of 1.1 m/kg | KG. | 70.72 | 47 | 3323.84 | 1619.5
|  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") with conversion factor of 3 Kg/Sq. meter | KG. | 28.5 | 70 | 1995 | 2187.5
[6 empty] | 14551.76 | 13961.4
16 |  | COST OF MATERIALS |  |  |  | 1549801.04 | 1230203.47
17 |  | ADD:3% CONTINGENCIES |  |  |  | 46494.0312 | 36906.1041
18 |  | ADD:2% STORAGE CHARGES |  |  |  | 30996.0208 | 24604.0694
19 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 30996.0208 | 24604.0694
20 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 232470.156 | 184530.5205
21 |  | A |  |  |  | 1890757.2688 | 1500848.2334
22 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899 | 6160
23 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257 | 1050
PLATE TYPE WITH SALT &COAL
24 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456 | 1260
25 |  | CARTING OF RSJ POLE AT WORK SITE | NO. | 2 | 246 | 492 | 440
26 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575 | 550
27 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564 | 11564
28 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550 | 550
ON T/C
|  | PLINTH (3.34*3.34*1.5MTR) FOR MOUNTING X-MER |  |  | ---LS--- | 65715.44 | 105600
|  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
|  | HINGERS, STOPPERS (Lumsum) |  | 1 | 770 | 770 | 770
|  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630 | 630
|  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.26 | 5900 | 1534 | 1670.5077
29 |  | LABOUR CHARGES… |  |  |  | 96142.44 | 134944.5077
30 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 14421.366 | 20241.6762
31 |  | B |  |  |  | 110563.806 | 155186.1839
32 |  | A+B |  |  |  | 2001321.0748 | 1656034.4173
|  | TOTAL ESTIMATE |  |  | Say Rs. | 2001321 | 1656034 | 345287 | 20.8502
345287
267934
77353

## 37SDT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 37
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER- SDT - 24 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING |  |  |  | 16986
|  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
|  | (e) C.I. Earthing pipe 100 mm dia,13 mm thick | No. | 2 | 6136 | 12272
|  | (f) GI Earthing strip (50x6mm) | Kg. | 50 | 68 | 3400
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 22232
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA) | No. | 1 | 10920 | 10920
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
10 | 44 06 02 0023 | 11 KVSPECIAL DESIGNED TRANSFORMER- SDT 24 AMP. | NO. | 1 | 112000 | 112000
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2616.4
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 3.2 | 9.6
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 65 | 780
2616.4
12 |  | COST OF MATERIALS |  |  |  | 180878.4
13 |  | ADD:3% CONTINGENCIES |  |  |  | 5426.352
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 3617.568
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3617.568
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 27131.76
17 |  | A |  |  |  | 220671.648
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 5900 | 5900
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
20 |  | ERECTION OF EARTHING CHAMBER | NO. | 2 | 2000 | 4000
EXCAVATION OF EART PIT SALT, CHARCOAL & BENTONITE
21 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
22 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
23 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
24 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
25 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
26 |  | INSTALLATION OF IDMT RELAY, CT COIL |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
27 |  | LABOUR CHARGES… |  |  |  | 19870
28 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2980.5
29 |  | B |  |  |  | 22850.5
30 |  | A+B |  |  |  | 243522.148
|  | TOTAL ESTIMATE |  |  | Say Rs. | 243522

## 38SDT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 38
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV ERECTION OF SPECIAL DESIGNED TRANSFORMER - SDT- 30 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING |  |  |  | 16986
|  | EARTHING FOR POLE NEUTRAL & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
|  | (e) C.I. Earthing pipe 100 mm dia,13 mm thick | No. | 2 | 6136 | 12272
|  | (f) GI Earthing strip (50x6mm) | Kg. | 50 | 68 | 3400
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 22232
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA) | No. | 1 | 10920 | 10920
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
10 | 44 06 02 0023 | 11 KV SPECIAL DESIGNED TRANSFORMER-SDT 30 AMP. | NO. | 1 | 135000 | 135000
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2616.4
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 13 02 00 0006 | (e) Fuse element-10 Amp | No | 3 | 14 | 42
| 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 18 | 0.7 | 12.6
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
| 04 15 00 0019 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 6 | 18.5 | 111
| 04 15 00 0003 | (i) Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 2 | 8.9 | 17.8
| 04 16 00 0007 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 9 | 5.5 | 49.5
| 04 16 00 0006 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 3.2 | 9.6
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 65 | 780
2616.4
12 |  | COST OF MATERIALS |  |  |  | 203878.4
13 |  | ADD:3% CONTINGENCIES |  |  |  | 6116.352
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 4077.568
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4077.568
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 30581.76
17 |  | A |  |  |  | 248731.648
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 5900 | 5900
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
20 |  | ERECTION OF EARTHING CHAMBER | NO. | 2 | 2000 | 4000
EXCAVATION OF EART PIT SALT, CHARCOAL & BENTONITE
21 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
22 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
23 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
24 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
25 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
26 |  | INSTALLATION OF IDMT RELAY, CT COIL |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
27 |  | LABOUR CHARGES… |  |  |  | 19870
28 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2980.5
29 |  | B |  |  |  | 22850.5
30 |  | A+B |  |  |  | 271582.148
|  | TOTAL ESTIMATE |  |  | Say Rs. | 271582

## 39PAT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 39
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 24.7 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING FOR POLE PAT BODY & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 22232
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA, 5P10) | No. | 1 | 10920 | 10920
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
10 | 44 06 02 0023 | 11 KV PILOT ADVANCE TRANSFORMER - PAT 24.7 AMP. | NO. | 1 | 190635 | 190635
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2365.5
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 65 | 780
2365.5
12 |  | COST OF MATERIALS |  |  |  | 243590.5
13 |  | ADD:3% CONTINGENCIES |  |  |  | 7307.715
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 4871.81
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4871.81
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 36538.575
17 |  | A |  |  |  | 297180.41
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 5900 | 5900
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
20 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
21 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
22 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
23 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
24 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
25 |  | INSTALLATION OF IDMT RELAY, CT |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
26 |  | LABOUR CHARGES… |  |  |  | 15870
27 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2380.5
28 |  | B |  |  |  | 18250.5
29 |  | A+B |  |  |  | 315430.91
|  | TOTAL ESTIMATE |  |  | Say Rs. | 315431

## 40PAT
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 40
RE/CITY COST DATA FOR THE YEAR 2019-20
11/0.433 KV ERECTION OF PILOT ADVANCE TRANSFORMER - PAT- 54 AMP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 9884
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 1 | 834 | 834
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
9884
3 |  | Gang operated three pole double throw change over switch | Set | 1 | 7611 | 7611
4 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
5 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
6 |  | EARTHING FOR POLE PAT BODY & | NO. | 3 | 438 | 1314
LIGHTENING ARRESTOR (PLATE TYPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
7 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimbing device | NO. | 2 | 120 | 240
8 |  | For Protection System |  |  |  | 33152
|  | (a) IDMT RELAY | No. | 1 | 6515 | 6515
|  | (b) HT 11KV C T coil (30/1, 15 VA, 5P10) | No. | 2 | 10920 | 21840
|  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 61 | 4270
|  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 527 | 527
9 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
10 | 44 06 02 0023 | 11 KV PILOT ADVANCE TRANSFORMER- PAT 54 AMP. | NO. | 1 | 278298 | 278298
11 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2365.5
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasle or Rabbit | No | 6 | 110 | 660
| 26 13 00 0002 | (l) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (m) Side Clamp | NO. | 12 | 65 | 780
2365.5
12 |  | COST OF MATERIALS |  |  |  | 342173.5
13 |  | ADD:3% CONTINGENCIES |  |  |  | 10265.205
14 |  | ADD:2% STORAGE CHARGES |  |  |  | 6843.47
15 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 6843.47
16 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 51326.025
17 |  | A |  |  |  | 417451.67
18 |  | LABOUR CHARGES FOR ERECTION OF SDT/PAT INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,Change Over Switch,
|  | ETC. | NO. | 1 | 5900 | 5900
19 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
20 |  | LAYING OF UNDER GROUND 2C 2.5SQMM CABLE | MTR | 70 | 30 | 2100
21 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
22 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
23 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
24 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
25 |  | INSTALLATION OF IDMT RELAY, CT COIL |  |  | ---LS--- | 550
& CONTROL WIRING IN PANEL
26 |  | LABOUR CHARGES… |  |  |  | 15870
27 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2380.5
28 |  | B |  |  |  | 18250.5
29 |  | A+B |  |  |  | 435702.17
|  | TOTAL ESTIMATE |  |  | Say Rs. | 435702

## 41
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 41
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 1 PH 2 WIRE USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2017 | 40340
2 |  | GUY SETS WITH PREFORMED FITTING. | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 40 | 81 | 3240
WITH FITTING VIZ. U CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | ALL ALU. ALLOY CONDUCTOR 34MM2 SIZE | KM. | 2.06 | 19989 | 41177.34
OF PHASES, NEUTRAL AND ST. LIGHT
| 01 02 00 0031 | ALL ALU. ALLOY CONDUCTOR 34MM2 | KM | 2.06 | 19989 | 41177.34
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 2084.8
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2.4 | 70 | 168
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 14.24 | 70 | 996.8
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 1 | 120 | 120
| 2615 00 0001/2 | (d) Line spacers for 2 wire line | NO | 40 | 20 | 800
|  | (Considering 2 spacers / span) |  |  |  | 2084.8
7 |  | COST OF MATERIALS |  |  |  | 97932.14
8 |  | ADD:3% CONTINGENCIES |  |  |  | 2937.9642
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 1958.6428
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1958.6428
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 14689.821
12 |  | A |  |  |  | 119477.2108
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF MATERIALS ON TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 20 | 757 | 15140
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 2 | 1373 | 2746
18 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
SALT EARTHING WITH AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 40 | 9 | 360
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 40015
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6002.25
24 |  | B |  |  |  | 46017.25
25 |  | A+B |  |  |  | 165494.4608
|  | TOTAL ESTIMATE |  |  | Say Rs. | 165494

## 42
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 42
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN-50 MTR)WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2017 | 40340
2 |  | GUY SETS WITH PREFORMED FITTING. | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 60 | 81 | 4860
WITH FITTING VIZ. U CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 | 01 02 00 0031 | ALL ALU. ALLOY CONDUCTOR 34MM2 SIZE | KM. | 3.09 | 19989 | 61766.01
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 3043.2
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2.4 | 70 | 168
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 21.36 | 70 | 1495.2
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 1.5 | 120 | 180
| 26 15 00 0022 | (d) Line spacers for 3 wire line | NO | 40 | 30 | 1200
|  | (Considering 2 spacers / span) |  |  |  | 3043.2
7 |  | COST OF MATERIALS |  |  |  | 121099.21
8 |  | ADD:3% CONTINGENCIES |  |  |  | 3632.9763
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 2421.9842
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2421.9842
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 18164.8815
12 |  | A |  |  |  | 147741.0362
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 20 | 757 | 15140
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 3 | 1373 | 4119
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 9 | 171
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES…. |  |  |  | 41199
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6179.85
24 |  | B |  |  |  | 47378.85
25 |  | A+B |  |  |  | 195119.8862
|  | TOTAL ESTIMATE |  |  | Say Rs. | 195120

## 43
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 43
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 1PH.3 WIRE FOR VERTICAL FORMATION USING 34 MM2 AAAC CONDUCTOR (SPAN - 30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 33 | 2017 | 66561
2 |  | GUY SETS WITH PREFORMED FITTING. | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 99 | 81 | 8019
WITH FITTING VIZ. U CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 | 01 02 00 0031 | ALL ALU. ALLOY CONDUCTOR 34MM2 SIZE | KM. | 3.09 | 19989 | 61766.01
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 5952.8
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 70 | 336
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 35.24 | 70 | 2466.8
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 1.5 | 120 | 180
| 26 15 00 0022 | (d) Line spacers for 3 wire line | NO | 99 | 30 | 2970
|  | (Considering 3 spacers / span) |  |  |  | 5952.8
7 |  | COST OF MATERIALS |  |  |  | 156794.81
8 |  | ADD:3% CONTINGENCIES |  |  |  | 4703.8443
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 3135.8962
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3135.8962
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 23519.2215
12 |  | A |  |  |  | 191289.6682
13 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 33 | 757 | 24981
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 3 | 1373 | 4119
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES…. |  |  |  | 60405
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9060.75
24 |  | B |  |  |  | 69465.75
25 |  | A+B |  |  |  | 260755.4182
|  | TOTAL ESTIMATE |  |  | Say Rs. | 260755

## 44
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 44
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING34 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2017 | 40340
2 |  | GUY SETS WITH PREFORMED | NO. | 5 | 984 | 4920
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
984
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 80 | 81 | 6480
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 19989 | 82354.68
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 19989 | 82354.68
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 4173.6
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 70 | 140
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 28.48 | 70 | 1993.6
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 40 | 45 | 1800
|  | (Considering 2 spacers / span) |  |  |  | 4173.6
7 |  | COST OF MATERIALS |  |  |  | 143508.28
8 |  | ADD:3% CONTINGENCIES |  |  |  | 4305.2484
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 2870.1656
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2870.1656
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 21526.242
12 |  | A |  |  |  | 175080.1016
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 20 | 757 | 15140
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
ITEM NO 22
17 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
18 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 5 | 364 | 1820
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 9 | 171
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5900 | 4425
22 |  | LABOUR CHARGES… |  |  |  | 41323
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6198.45
24 |  | B |  |  |  | 47521.45
25 |  | A+B |  |  |  | 222601.5516
|  | TOTAL ESTIMATE |  |  | Say Rs. | 222602

## 45
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 45
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 9 MTR RSJ POLES 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 33 | 2017 | 66561
2 |  | GUY SETS WITH PREFORMED | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 132 | 81 | 10692
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 19989 | 82354.68
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 19989 | 82354.68
6 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 802 | 26466
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 65 | 130
802
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 9238
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 18 | 70 | 1260
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 46.9 | 70 | 3283
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 45 | 4455
|  | (Considering 3 spacers / span) |  |  |  | 9238
8 |  | COST OF MATERIALS |  |  |  | 209807.68
9 |  | ADD:3% CONTINGENCIES |  |  |  | 6294.2304
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4196.1536
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4196.1536
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 31471.152
13 |  | A |  |  |  | 255965.3696
14 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
17 |  | LABOUR CHARGES FOR | NO. | 33 | 757 | 24981
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
23 |  | LABOUR CHARGES… |  |  |  | 61778
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9266.7
25 |  | B |  |  |  | 71044.7
26 |  | A+B |  |  |  | 327010.0696
|  | TOTAL ESTIMATE |  |  | Say Rs. | 327010

## 46
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 46
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 9 MTR RSJ POLES 34 MM2 AAAC CONDUCTOR(SPAN-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 33 | 10478 | 345774
2 |  | GUY SETS WITH PREFORMED | NO. | 6 | 984 | 5904
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
984
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 132 | 81 | 10692
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 19989 | 82354.68
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 19989 | 82354.68
6 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 802 | 26466
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 65 | 130
802
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 8559
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 55.2 | 70 | 3864
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 45 | 4455
|  | (Considering 3 spacers / span) |  |  |  | 8559
8 |  | COST OF MATERIALS |  |  |  | 488395.68
9 |  | ADD:3% CONTINGENCIES |  |  |  | 14651.8704
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 9767.9136
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 9767.9136
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 73259.352
13 |  | A |  |  |  | 595842.7296
14 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
17 |  | LABOUR CHARGES FOR | NO. | 33 | 1268 | 41844
ERECTION OF RSJ POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
22 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5900 | 137706
23 |  | LABOUR CHARGES… |  |  |  | 211037
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 31655.55
25 |  | B |  |  |  | 242692.55
26 |  | A+B |  |  |  | 838535.2796
|  | TOTAL ESTIMATE |  |  | Say Rs. | 838535

## 47
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 47
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE VERTICAL FORMATION USING 10 MTR PSC POLES 34 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 20 | 3505 | 70100
2 |  | GUY SETS WITH PREFORMED | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 132 | 81 | 10692
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AAAC 34MM2 SIZE FOR PHASES & NEUTRAL | KM. | 4.12 | 19989 | 82354.68
| 01 02 00 0031 | AAA Conductor 34MM2 | KM | 4.12 | 19989 | 82354.68
6 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 20 | 802 | 16040
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 65 | 130
802
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 6804
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 55.2 | 70 | 3864
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 60 | 45 | 2700
|  | (Considering 3 spacers / span) |  |  |  | 6804
8 |  | COST OF MATERIALS |  |  |  | 200978.68
9 |  | ADD:3% CONTINGENCIES |  |  |  | 6029.3604
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4019.5736
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4019.5736
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 30146.802
13 |  | A |  |  |  | 245193.9896
14 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
17 |  | LABOUR CHARGES FOR | NO. | 20 | 1815 | 36300
ERECTION OF RSJ POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 60 | 9 | 540
22 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
23 |  | LABOUR CHARGES… |  |  |  | 62331
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9349.65
25 |  | B |  |  |  | 71680.65
26 |  | A+B |  |  |  | 316874.6396
|  | TOTAL ESTIMATE |  |  | Say Rs. | 316875

## 48
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 48
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE FOR AG. PURPOSE AND VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN- 50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2017 | 40340
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 5 | 975 | 4875
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 80 | 81 | 6480
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 31288 | 96679.92
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 31288 | 96679.92
6 |  | -DO- BUT 34MM2 AAAC( NEUTRAL WIRE) | KM. | 1.03 | 19989 | 20588.67
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 1.03 | 19989 | 20588.67
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 4173.6
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 70 | 140
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 28.48 | 70 | 1993.6
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 40 | 45 | 1800
|  | (Considering 2 spacers / span) |  |  |  | 4173.6
8 |  | COST OF MATERIALS |  |  |  | 178377.19
9 |  | ADD:3% CONTINGENCIES |  |  |  | 5351.3157
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 3567.5438
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3567.5438
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 26756.5785
13 |  | A |  |  |  | 217620.1718
14 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
17 |  | LABOUR CHARGES FOR | NO. | 20 | 757 | 15140
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 5 | 364 | 1820
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 9 | 171
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5900 | 4425
23 |  | LABOUR CHARGES… |  |  |  | 41323
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6198.45
25 |  | B |  |  |  | 47521.45
26 |  | A+B |  |  |  | 265141.6218
|  | TOTAL ESTIMATE |  |  | Say Rs. | 265142

## 49
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 49
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING PSC POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 33 | 2017 | 66561
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 132 | 81 | 10692
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 31288 | 96679.92
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 31288 | 96679.92
6 |  | -DO- BUT 34MM2 AAAC( NEUTRAL WIRE) | KM. | 1.03 | 19989 | 20588.67
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 1.03 | 19989 | 20588.67
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 8853
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 55.4 | 70 | 3878
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 45 | 4455
|  | (Considering 2 spacers / span) |  |  |  | 8853
8 |  | COST OF MATERIALS |  |  |  | 217870.59
9 |  | ADD:3% CONTINGENCIES |  |  |  | 6536.1177
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4357.4118
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4357.4118
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 32680.5885
13 |  | A |  |  |  | 265802.1198
14 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
17 |  | LABOUR CHARGES FOR | NO. | 33 | 757 | 24981
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
19 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
23 |  | LABOUR CHARGES… |  |  |  | 61778
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9266.7
25 |  | B |  |  |  | 71044.7
26 |  | A+B |  |  |  | 336846.8198
|  | TOTAL ESTIMATE |  |  | Say Rs. | 336847

## 50
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 50
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.4 WIRE FOR CITY/GIDC PURPOSE AND VERTICAL FORMATION USING 9 MTR RSJ POLE 55 MM2 AAAC CONDUCTOR(Span-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9 MTR | NO. | 33 | 10478 | 345774
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 984 | 5904
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
984
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 132 | 81 | 10692
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 31288 | 96679.92
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 31288 | 96679.92
6 |  | -DO- BUT 34MM2 AAAC( NEUTRAL WIRE) | KM. | 1.03 | 19989 | 20588.67
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 1.03 | 19989 | 20588.67
7 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 802 | 26466
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 65 | 130
802
8 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 8559
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 55.2 | 70 | 3864
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2 | 120 | 240
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 99 | 45 | 4455
|  | (Considering 3 spacers / span) |  |  |  | 8559
9 |  | COST OF MATERIALS |  |  |  | 523309.59
10 |  | ADD:3% CONTINGENCIES |  |  |  | 15699.2877
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 10466.1918
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 10466.1918
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 78496.4385
14 |  | A |  |  |  | 638437.6998
15 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118
DESTINATION
16 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
17 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
18 |  | LABOUR CHARGES FOR | NO. | 33 | 1268 | 41844
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
19 |  | STRINGING OF CONDUCTOR | KM. | 4 | 1373 | 5492
20 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
21 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
22 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
23 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5900 | 137706
24 |  | LABOUR CHARGES… |  |  |  | 211037
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 31655.55
26
26 |  | B |  |  |  | 242692.55
27 |  | A+B |  |  |  | 881130.2498
|  | TOTAL ESTIMATE |  |  | Say Rs. | 881130

## 51
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 51
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (WEASEL)(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 20 | 2017 | 40340
2 |  | GUY SETS WITH PREFORMED FITTINGS | NO. | 5 | 975 | 4875
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 110 | 81 | 8910
WITH FITTING VIZ. V CLAMP AND
|  | GI BOLT | No
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp |  | 1 | 56 | 56
81
5 | 01 02 00 0031 | 34MM2 AAAC CONDUCTOR | KM. | 5.15 | 19989 | 102943.35
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 6232
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 70 | 140
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 35.6 | 70 | 2492
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 60 | 55 | 3300
|  | (Considering 3 spacers / span) |  |  |  | 6232
7 |  | COST OF MATERIALS |  |  |  | 168540.35
8 |  | ADD:3% CONTINGENCIES |  |  |  | 5056.2105
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 3370.807
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3370.807
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 25281.0525
12 |  | A |  |  |  | 205619.227
13 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 20 | 757 | 15140
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1373 | 6865
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 5 | 364 | 1820
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 60 | 9 | 540
|  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5900 | 4425
21 |  | LABOUR CHARGES…. |  |  |  | 43065
22 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6459.75
23 |  | B |  |  |  | 49524.75
24 |  | A+B |  |  |  | 255143.977
|  | TOTAL ESTIMATE |  |  | Say Rs. | 255144

## 52
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 52
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PH.5WIRE FOR VERTICAL FORMATION USING 34MM2AAAC CONDUCTOR (Span-30 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M 200 KG | NO. | 33 | 2017 | 66561
2 |  | GUY SETS WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
3 |  | EARTHING OF POLES (COIL TYPE). | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
4 |  | L.T. SHACKLE INSULATOR COMP. | NO. | 165 | 81 | 13365
WITH FITTING VIZ. V CLAMP AND
|  | GI BOLT | No
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp |  | 1 | 56 | 56
81
5 | 01 02 00 0031 | 34MM2 AAAC CONDUCTOR | KM. | 5.15 | 19989 | 102943.35
6 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 9763
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 53.4 | 70 | 3738
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 99 | 55 | 5445
|  | (Considering 3 spacers / span) |  |  |  | 9763
7 |  | COST OF MATERIALS |  |  |  | 207128.35
8 |  | ADD:3% CONTINGENCIES |  |  |  | 6213.8505
9 |  | ADD:2% STORAGE CHARGES |  |  |  | 4142.567
10 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4142.567
11 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 31069.2525
12 |  | A |  |  |  | 252696.587
13 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 33 | 757 | 24981
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1373 | 6865
18 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
19 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
20 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
|  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
21 |  | LABOUR CHARGES…. |  |  |  | 63151
22 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 9472.65
23 |  | B |  |  |  | 72623.65
24 |  | A+B |  |  |  | 325320.237
|  | TOTAL ESTIMATE |  |  | Say Rs. | 325320

## 53
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 53
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING 9 MTR RSJ POLE 34 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*100*9 MTR | NO. | 33 | 10478 | 345774
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 165 | 81 | 13365
WITH H/W & PREFORM FITTINGS.
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AL.ALLOY CONDUCTOR 34 MM2 SIZE. | KM. | 5.15 | 19989 | 102943.35
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 5.15 | 19989 | 102943.35
6 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 0 | 19989 | 0
AND STREET LIGHT
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 0 | 19989 | 0
7 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 802 | 26466
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 65 | 130
802
8 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
|  | BINDING WIRE,LINE SPACER ETC. |  |  |  | 10043
WITH PREFORMED FITTINGS
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 61.4 | 70 | 4298
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 99 | 55 | 5445
|  | (Considering 3 spacers / span) |  |  |  | 10043
9 |  | COST OF MATERIALS |  |  |  | 513087.35
10 |  | ADD:3% CONTINGENCIES |  |  |  | 15392.6205
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 10261.747
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 10261.747
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 76963.1025
14 |  | A |  |  |  | 625966.567
15 |  | CARTING OF RSJ POLE AT | NO. | 33 | 246 | 8118
DESTINATION
16 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
17 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
18 |  | LABOUR CHARGES FOR | NO. | 33 | 1268 | 41844
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
19 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1373 | 6865
20 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
21 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
22 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
23 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5900 | 137706
24 |  | LABOUR CHARGES…. |  |  |  | 212410
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 31861.5
26 |  | B |  |  |  | 244271.5
27 |  | A+B |  |  |  | 870238.067
|  | TOTAL ESTIMATE |  |  | Say Rs. | 870238

## 54
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 54
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PHASE 5WIRE FOR AG PURPOSE. VERTICAL FORMATION USING 55 MM2 AAAC CONDUCTOR(SPAN-50 MTR) WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2017 | 40340
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 5 | 975 | 4875
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 100 | 81 | 8100
WITH H/W & PREFORM FITTINGS.
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 31288 | 96679.92
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 31288 | 96679.92
6 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 2.06 | 19989 | 41177.34
AND STREET LIGHT
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 2.06 | 19989 | 41177.34
7 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
|  | BINDING WIRE,LINE SPACER ETC. |  |  |  | 6232
WITH PREFORMED FITTINGS
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 2 | 70 | 140
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 35.6 | 70 | 2492
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 60 | 55 | 3300
|  | (Considering 3 spacers / span) |  |  |  | 6232
8 |  | COST OF MATERIALS |  |  |  | 202644.26
9 |  | ADD:3% CONTINGENCIES |  |  |  | 6079.3278
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4052.8852
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4052.8852
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 30396.639
13 |  | A |  |  |  | 247225.9972
14 |  | CARTING OF PSC POLE AT | NO. | 20 | 246 | 4920
DESTINATION
15 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
16 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
17 |  | LABOUR CHARGES FOR | NO. | 20 | 757 | 15140
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
18 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1373 | 6865
19 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 5 | 364 | 1820
20 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT AND COAL
21 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 60 | 9 | 540
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.75 | 5900 | 4425
23 |  | LABOUR CHARGES…. |  |  |  | 43065
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6459.75
25 |  | B |  |  |  | 49524.75
26 |  | A+B |  |  |  | 296750.7472
|  | TOTAL ESTIMATE |  |  | Say Rs. | 296751

## 55
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 55
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE 3PHASE 5WIRE VERTICAL FORMATION USING RSJ POLE 55 MM2 AAAC CONDUCTOR (SPAN 30 MTR)WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS for 1KM | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*100*9 MTR | NO. | 33 | 10478 | 345774
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 262 | 8646
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 795 | 4770
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
795
4 |  | LT SHACKLE INSULATOR COMPL. | NO. | 165 | 81 | 13365
WITH H/W & PREFORM FITTINGS.
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
5 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 3.09 | 31288 | 96679.92
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 3.09 | 31288 | 96679.92
6 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 2.06 | 19989 | 41177.34
AND STREET LIGHT
| 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 | KM | 2.06 | 19989 | 41177.34
7 |  | VERTICAL FORMATION FOR 4 WIRE LT LINE | SET | 33 | 802 | 26466
| 2609000014 | C TYPE FORMATION | NO | 1 | 672 | 672
| 2601000049 | SIDE CLAMP | NO | 2 | 65 | 130
802
8 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
|  | BINDING WIRE,LINE SPACER ETC. |  |  |  | 10043
WITH PREFORMED FITTINGS
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 61.4 | 70 | 4298
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 2.5 | 120 | 300
| 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 99 | 55 | 5445
|  | (Considering 3 spacers / span) |  |  |  | 10043
9 |  | COST OF MATERIALS |  |  |  | 546921.26
10 |  | ADD:3% CONTINGENCIES |  |  |  | 16407.6378
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 10938.4252
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 10938.4252
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 82038.189
14 |  | A |  |  |  | 667243.9372
15 |  | CARTING OF RSJ POLE AT | NO. | 33 | 246 | 8118
DESTINATION
16 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
17 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
18 |  | LABOUR CHARGES FOR | NO. | 33 | 1268 | 41844
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
19 |  | STRINGING OF CONDUCTOR | KM. | 5 | 1373 | 6865
20 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
21 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827
EARTHING WITH SALT AND COAL
22 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 99 | 9 | 891
23 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 23.34 | 5900 | 137706
24 |  | LABOUR CHARGES…. |  |  |  | 212410
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 31861.5
26 |  | B |  |  |  | 244271.5
27 |  | A+B |  |  |  | 911515.4372
|  | TOTAL ESTIMATE |  |  | Say Rs. | 911515

## 56
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 56
RE/CITY COST DATA FOR THE YEAR 2019-20
L.T. LINE ADDING OF ONE WIRE IN VERTICAL FORMATION USING55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 2 | 984 | 1968
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
984
2 |  | LT SHACKLE INSULATOR COMPL. | NO. | 20 | 81 | 1620
WITH FITTING VIZ."U "CLAMP AND
GI BOLT
| 20 02 00 0001 | (a) LT Shackle Insulator | No | 1 | 14 | 14
| 20 10 00 0002 | (b) LT Shackle Bolt | No | 1 | 11 | 11
| 26 01 00 0040 | (c) U clamp | No | 1 | 56 | 56
81
3 |  | AL.ALLOY CONDUCTOR 55 MM2 SIZE. | KM. | 1.03 | 31288 | 32226.64
| 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 | KM | 1.03 | 31288 | 32226.64
4 |  | SUNDRY MATERIALS SUCH AS BOLTS
NUTS/PG CLAMPS,GI WIRE,BINDING TAPE &
BINDING WIRE,LINE SPACER ETC.
|  | WITH PREFORMED FITTINGS |  |  |  | 1035
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 0.5 | 70 | 35
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 7 | 70 | 490
| 01 01 00 0003 | (c) Alu. Binding wire | KG | 0.5 | 120 | 60
| 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 10 | 45 | 450
|  | (Considering 2 spacers / span) |  |  |  | 1035
5 |  | COST OF MATERIALS |  |  |  | 36849.64
6 |  | ADD:3% CONTINGENCIES |  |  |  | 1105.4892
7 |  | ADD:2% STORAGE CHARGES |  |  |  | 736.9928
8 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 736.9928
9 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 5527.446
10 |  | A |  |  |  | 44956.5608
11 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
12 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 287.5
13 |  | STRINGING OF CONDUCTOR | KM. | 1 | 1373 | 1373
14 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 2 | 364 | 728
15 |  | LABOUR CHARGES FOR PROVIDING LINE SPACER | NO. | 19 | 9 | 171
16 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5900 | 1770
17 |  | LABOUR CHARGES… |  |  |  | 4729.5
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 709.425
19 |  | B |  |  |  | 5438.925
20 |  | A+B |  |  |  | 50395.4858
|  | TOTAL ESTIMATE |  |  | Say Rs. | 50395

## 57
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 57
RE/CITY COST DATA FOR THE YEAR 2019-20
SERVICE CONNECTION 3 PHASE 4 WIRE UP TO 5 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 6 | 60 | 360
2 | 16 07 00 0009 | SMC METER BOX 3-Phase | NO. | 1 | 882 | 882
|  | Three phase SMC meter box | NO. | 1 | 882 | 882
3 | 16 07 00 0003 | METAL METER BOX 1-Phase | NO. | 0 | 219 | 0
|  | Single Phase SMC meter Box | NO. | 0 | 219 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 73 | 219
4 | 04 01 00 0033 | PVC ALUM.4 CX6MM2 UN-ARMOURED CABLE | MTR | 35 | 26.96 | 943.6
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 298 | 298
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 298 | 298
termination of service (Service Angle)
6 | 16 01 00 0073 | 3 PHASE W.C. L.T. STATIC METER 10/60 AMP. | NO. | 1 | 1472 | 1472
7 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 75.1198
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 70 | 16.016
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 43 | 43
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw-20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 6 | 0.7 | 4.2
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
75.1198
9 |  | COST OF MATERIALS |  |  |  | 4687.7198
10 |  | ADD:3% CONTINGENCIES |  |  |  | 140.6316
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 93.7544
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 93.7544
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 703.158
14 |  | A |  |  |  | 5719.0182
15 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 355 | 355
SERVICE CONNECTION
16 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 774
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 116.1
18 |  | B |  |  |  | 890.1
19 |  | A+B |  |  |  | 6609.1182
|  | TOTAL ESTIMATE |  |  | Say Rs. | 6609

## 58
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 58
RE/CITY COST DATA FOR THE YEAR 2019-20
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 5 HP TO 10 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 6 | 60 | 360
2 |  | SMC METER BOX 3-Phase | NO. | 1 | 882 | 882
| 16 07 00 0009 | Three phase SMC meter box | NO. | 1 | 882 | 882
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 219 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 219 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 73 | 219
4 | 04 01 00 0034 | PVC ALUM.4 CX 10 MM2 UN-ARMOURED CABLE | MTR | 35 | 41.65 | 1457.75
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 298 | 298
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 298 | 298
termination of service (Service Angle)
6 | 16 01 00 0073 | 3 PHASE W.C. L.T. STATIC METER 10/60 AMP. | NO. | 1 | 1472 | 1472
7 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 75.1198
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 70 | 16.016
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 43 | 43
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 6 | 0.7 | 4.2
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
75.1198
9 |  | COST OF MATERIALS |  |  |  | 5201.8698
10 |  | ADD:3% CONTINGENCIES |  |  |  | 156.0561
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 104.0374
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 104.0374
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 780.2805
14 |  | A |  |  |  | 6346.2812
15 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 355 | 355
SERVICE CONNECTION
16 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 774
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 116.1
18 |  | B |  |  |  | 890.1
19 |  | A+B |  |  |  | 7236.3812
|  | TOTAL ESTIMATE |  |  | Say Rs. | 7236

## 59
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 59
RE/CITY COST DATA FOR THE YEAR 2019-20
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 10 HP TO 20 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 6 | 60 | 360
2 | 16 07 00 0009 | SMC METER BOX 3-Phase | NO. | 1 | 882 | 882
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 219 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 219 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 73 | 219
4 | 04 01 00 0035 | PVC ALUM.4 CX16MM2 UN-ARMOURED CABLE | MTR | 35 | 61.304 | 2145.64
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 298 | 298
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 298 | 298
termination of service (Service Angle)
6 | 16 01 00 0073 | 3 PHASE W.C. L.T. STATIC METER 10/60 AMP. | NO. | 1 | 1472 | 1472
7 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 75.1198
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 70 | 16.016
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 43 | 43
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 6 | 0.7 | 4.2
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 12 | 0.7 | 8.4
75.1198
9 |  | COST OF MATERIALS |  |  |  | 5889.7598
10 |  | ADD:3% CONTINGENCIES |  |  |  | 176.6928
11 |  | ADD:2% STORAGE CHARGES |  |  |  | 117.7952
12 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 117.7952
13 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 883.464
14 |  | A |  |  |  | 7185.507
15 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 355 | 355
SERVICE CONNECTION
16 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 774
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 116.1
18 |  | B |  |  |  | 890.1
19 |  | A+B |  |  |  | 8075.607
|  | TOTAL ESTIMATE |  |  | Say Rs. | 8076

## 60
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 60
RE/CITY COST DATA FOR THE YEAR 2019-20
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 20 HP TO 60 HP
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0014 | KIT-KAT FUSE 100 AMPS. | NO. | 6 | 228 | 1368
2 |  | SMC METER BOX 3-Phase | NO. | 1 | 882 | 882
| 16 07 00 0009 | Three phase SMC meter box for C.T. Operated meter | NO. | 1 | 882 | 882
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 219 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 219 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 73 | 219
4 | 04 01 00 0003 | 3.5 CORE 50MM2 PVC CABLE. | MTR | 35 | 137.82 | 4823.7
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 298 | 298
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 298 | 298
termination of service (Service Angle)
6 | 16 01 00 0069 | 3 PHASE L.T. STATIC METER 100/5 AMP. C. T. OPERATED. | NO. | 1 | 1589 | 1589
7 | 16 08 00 0046 | RING TYPE L. T. C. T. - 100/5 AMP. | SET | 1 | 735 | 735
8 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
9 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 95.8198
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 70 | 16.016
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 43 | 43
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0028 | (e) Screw - 75x8 ( for 100 Amp Fuse) | NO | 6 | 1.35 | 8.1
| 15 0100 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 13 01 00 0017 | (g) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 36 | 0.7 | 25.2
95.8198
10 |  | COST OF MATERIALS |  |  |  | 10448.5198
11 |  | ADD:3% CONTINGENCIES |  |  |  | 313.4556
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 208.9704
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 208.9704
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 1567.278
15 |  | A |  |  |  | 12747.1942
16 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 355 | 355
SERVICE CONNECTION
17 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 774
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 116.1
19 |  | B |  |  |  | 890.1
20 |  | A+B |  |  |  | 13637.2942
|  | TOTAL ESTIMATE |  |  | Say Rs. | 13637

## 61
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 61
RE/CITY COST DATA FOR THE YEAR 2019-20
SERVICE CONNECTION 3 PHASE 4 WIRE FROM 60 HP AND ABOVE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 0 | 40 | 0
1 | 13 03 00 0020 | KIT-KAT FUSE 200 AMPS. | NO. | 6 | 582 | 3492
2 |  | SMC METER BOX 3-Phase | NO. | 1 | 882 | 882
| 16 07 00 0009 | Three phase SMC meter box for C.T. Operated meter | NO. | 1 | 882 | 882
4 |  | METAL METER BOX 1- Phase | NO. | 0 | 219 | 0
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 0 | 219 | 0
3 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 3 | 73 | 219
4 | 04 01 00 0004 | 3.5 CORE 70MM2 PVC CABLE. | MTR | 35 | 184.08 | 6442.8
5 |  | ANGLE SUPPORT FOR TERMINATION OF | NO | 1 | 298 | 298
SERVICE
| 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 1 | 298 | 298
termination of service (Service Angle)
6 | 16 01 00 0070 | 3 PHASE L.T. STATIC METER 200/5 AMP. | NO. | 1 | 1589 | 1589
C. T. OPERATED.
7 | 16 08 00 0047 | RING TYPE L. T. C. T. - 200/5 AMP. | SET | 1 | 389 | 389
8 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
9 |  | SUNDRY MATERIAL SUCH AS PG
CLAMP,BINDING WIRE,TAPS,BOLT,PIECE OF
|  | PVC PIPE ,NUTS WITH PREFORM FITTING. |  |  |  | 151.9198
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.2288 | 70 | 16.016
| 28 01 00 0015 | (b) Rigid PVC Pipe- 1.5 Mtr | NO | 1 | 43 | 43
| 19 05 00 0002 | (c) LT Tape | Mtr | 2 | 1.4769 | 2.9538
| 15 05 00 0013 | (d) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 15 05 00 0028 | (e)Bolt type Screw - 1/8 x.2" ( for 200 Amp Fuse) | NO | 6 | 2.3 | 13.8
| 13 01 00 0006 | (f) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 13 01 00 0022 | (g) Tinned Copper Fuse Wire No.10(for 200 Amp. Fuse) | Grams | 108 | 0.7 | 75.6
151.9198
10 |  | COST OF MATERIALS |  |  |  | 13901.7198
11 |  | ADD:3% CONTINGENCIES |  |  |  | 417.0516
12 |  | ADD:2% STORAGE CHARGES |  |  |  | 278.0344
13 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 278.0344
14 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2085.258
15 |  | A |  |  |  | 16960.0982
16 |  | LABOUR CHARGES FOR LAYING OF | NO. | 1 | 355 | 355
SERVICE CONNECTION
17 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 774
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 116.1
19 |  | B |  |  |  | 890.1
20 |  | A+B |  |  |  | 17850.1982
|  | TOTAL ESTIMATE |  |  | Say Rs. | 17850
4000
13850

## 62
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 62
RE/CITY COST DATA FOR THE YEAR 2019-20
ESTIMATE FOR SINGLE PHASE SERVICE CONNECTION (UP TO 6 KW LOAD )
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 1 | 40 | 40
2 |  | METAL METER BOX BELOW 50 AMPS | NO. | 1 | 219 | 219
| 16 07 00 0001 | Single Phase SMC meter Box | NO. | 1 | 219 | 219
3 | 01 03 00 0003 | G.I.WIRE NO.10 (3.15 MM) | KG. | 1.5 | 70 | 105
4 | 19 01 00 0005 | PVC INSULATED PVC SHEATHED | MTR. | 35 | 6.85 | 239.75
2.5 MM2TWIN CORE CABLE
5 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 1 | 465 | 465
6 | 20 04 00 0001 | REEL INSULATOR | NO. | 60 | 0.55 | 33
7 | 20 05 00 0001 | EGG INSULATOR | NO. | 2 | 1.6 | 3.2
8 | 28 01 00 0015 | PVC PIPE 20 MM DIA (3 MTR PIECE) | NO | 1 | 43 | 43
9 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
10 |  | COST OF SCREW,BOLTS,BLACK TAPS,
|  | BINDING WIRE ,EARTHING BOLTS ETC. WITH |  |  |  | 5.254
PREFORMED FITTING.
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.0572 | 70 | 4.004
| 15 05 00 0013 | (b) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (c) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.7 | 0.7
5.254
11 |  | COST OF MATERIALS |  |  |  | 1591.204
12 |  | ADD:3% CONTINGENCIES |  |  |  | 47.7361
13 |  | ADD:2% STORAGE CHARGES |  |  |  | 31.8241
14 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 31.8241
15 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 238.6806
16 |  | A |  |  |  | 1941.2689
17 |  | LABOUR CHARGES FOR LAYING OF |  | 1 | 258 | 258
SERVICE CONNECTION
18 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 677
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 101.55
20 |  | B |  |  |  | 778.55
21 |  | A+B |  |  |  | 2719.8189
|  | TOTAL ESTIMATE |  |  | Say Rs. | 2720
725
1995

## 63
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 63
RE/CITY COST DATA FOR THE YEAR 2019-20
ESTIMATE FOR SINGLE PHASE STREET LIGHT CONNECTION
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 1 | 40 | 40
2 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 1 | 465 | 465
3 | 21 05 00 0002 | ICDP SWITCH 32 AMPS./30 AMPS. | NO. | 1 | 140 | 140
4 | 19 01 00 0005 | PVC INSULATED PVC SHEATHED | MTR | 35 | 6.85 | 239.75
2.5 MM2TWIN CORE CABLE
5 | 30 99 00 0002 | CLAMP FOR FIXING PVC PIPE | NO. | 1 | 65 | 65
(M.S.CLAMP FOR ST.LIGHT FIXTURE)
6 | 28 01 00 0015 | PVC PIPE 20 MM DIA 3 MTR | NO | 1 | 43 | 43
7 |  | METAL METER BOX FOR 1 PHASE | NO. | 1 | 219 | 219
| 16 07 00 0003 | Single Phase SMC meter Box | NO. | 1 | 219 | 219
8 | 21 07 00 0060 | HOOK CLAMP FOR FIXING (DISTRIBUTION CLAMP) | NO. | 2 | 60 | 120
9 |  | EARTH TERMINAL | NO. | 1 | 438 | 438
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
10 |  | SUNDRY MATERIAL |  |  |  | 5.254
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.0572 | 70 | 4.004
| 15 05 00 0013 | (b) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (c) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.7 | 0.7
5.254
11 |  | COST OF MATERIALS |  |  |  | 1775.004
12 |  | ADD:3% CONTINGENCIES |  |  |  | 53.2501
13 |  | ADD:2% STORAGE CHARGES |  |  |  | 35.5001
14 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 35.5001
15 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 266.2506
16 |  | A |  |  |  | 2165.5049
17 |  | LABOUR CHARGES FOR LAYING OF | No | 1 | 258 | 258
SERVICE CONNECTION
18 |  | ERECTION OF EARTHING COIL/ | NO. | 1 | 419 | 419
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 677
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 101.55
20 |  | B |  |  |  | 778.55
21 |  | A+B |  |  |  | 2944.0549
|  | TOTAL ESTIMATE |  |  | Say Rs. | 2944

## 64
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 64
RE/CITY COST DATA FOR THE YEAR 2019-20
ESTIMATE FOR SINGLE PHASE STREET LIGHT FIXTURE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 1 | 40 | 40
2 | 30 06 00 0007 | STREET LIGHT FIXURE COMPLETE WITH HOLDER | NO. | 1 | 575 | 575
| /0004 | REFLECTOR NIPPLE etc.
3 | 19 01 00 0005 | PVC INSULATED PVC SHETHED | MTR. | 8 | 6.85 | 54.8
2.5 MM2 TWIN CORE CABLE
4 | 30 99 00 0002 | CLAMP FOR FIXING STREET LIGHT FIXURE | NO. | 2 | 65 | 130
INCLUDING BOLT & NUTS.
9 |  | EARTH TERMINAL | NO. |  | 438 | 0
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
5 |  | SUNDRY MATERIAL |  |  |  | 1.25
| 15 05 00 0013 | (a) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (b) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.7 | 0.7
1.25
6 |  | COST OF MATERIALS |  |  |  | 801.05
7 |  | ADD:3% CONTINGENCIES |  |  |  | 24.0315
8 |  | ADD:2% STORAGE CHARGES |  |  |  | 16.021
9 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 16.021
10 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 120.1575
11 |  | A |  |  |  | 977.281
12 |  | LABOUR CHARGES FOR PROVIDING STREET |  |  | ---L.S--- | 227
LIGHT FIXURE
18 |  | ERECTION OF EARTHING COIL/ | NO. |  | 419 | 0
PLATE TYPE WITH SALT &COAL
|  | LABOUR CHARGES… |  |  |  | 227
13 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 34.05
14 |  | B |  |  |  | 261.05 | 41.6
0.5
15 |  | A+B |  |  |  | 1238.331 | 35.25
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1238 | 514

## 65
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 65
RE/CITY COST DATA FOR THE YEAR 2019-20
LT LINE 1PH 2 WIRE USING ABC OF SIZE 1x 35 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 25 | 2017 | 50425
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 262 | 6550
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 | 405000019 | 1x 35 Sq.mm + 1x35 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 44527 | 46753.35
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | 4 | 135 | 540
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
52883.35
|  | COST OF MATERIALS |  |  |  | 115708.35
9 |  | ADD:3% CONTINGENCIES |  |  |  | 3471.2505
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 2314.167
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 2314.167
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 17356.2525
|  | A |  |  |  | 141164.187
13 |  | CARTING OF PSC POLE AT | NO. | 25 | 246 | 6150
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 25 | 757 | 18925
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 419 | 10475
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of AB Cable including fittings of All Accessories | KM | 1 | 5883 | 5883
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 2 | 11 | 22
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 49924
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7488.6
24 |  | B |  |  |  | 57412.6
25 |  | A+B |  |  |  | 198576.787
|  | TOTAL ESTIMATE |  |  | Say Rs. | 198577

## 66
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 66
RE/CITY COST DATA FOR THE YEAR 2019-20
LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 35 SQ MM + 1x 16 SQ MM + 1x 25 SQ MM ON 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 25 | 2017 | 50425
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 262 | 6550
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 | 405000023 | 3x 35 Sq.mm +1x16 sq.mm. +1x25 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 89796 | 94285.8
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | 4 | 135 | 540
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
100415.8
|  | COST OF MATERIALS |  |  |  | 163240.8
9 |  | ADD:3% CONTINGENCIES |  |  |  | 4897.224
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 3264.816
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3264.816
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 24486.12
|  | A |  |  |  | 199153.776
13 |  | CARTING OF PSC POLE AT | NO. | 25 | 246 | 6150
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 25 | 757 | 18925
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 419 | 10475
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of AB Cable including fittings of All Accessories | KM | 1 | 14707 | 14707
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 58770
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 8815.5
24 |  | B |  |  |  | 67585.5
25 |  | A+B |  |  |  | 266739.276
|  | TOTAL ESTIMATE |  |  | Say Rs. | 266739

## 67
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 67
RE/CITY COST DATA FOR THE YEAR 2019-20
LT LINE 3PH 4 WIRE USING ABC OF SIZE 3x 50 SQ MM + 1x 25 SQ MM + 1x 35 SQ MM ON 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 25 | 2017 | 50425
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 262 | 6550
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 | 405000023 | 3x 50 Sq.mm +1x25 sq.mm. +1x35 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 125513 | 131788.65
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | 4 | 135 | 540
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
137918.65
|  | COST OF MATERIALS |  |  |  | 200743.65
9 |  | ADD:3% CONTINGENCIES |  |  |  | 6022.3095
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 4014.873
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4014.873
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 30111.5475
|  | A |  |  |  | 244907.253
13 |  | CARTING OF PSC POLE AT | NO. | 25 | 246 | 6150
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 25 | 757 | 18925
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 419 | 10475
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of AB Cable including fittings of All Accessories | KM | 1 | 14707 | 14707
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 58770
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 8815.5
24 |  | B |  |  |  | 67585.5
25 |  | A+B |  |  |  | 312492.753
|  | TOTAL ESTIMATE |  |  | Say Rs. | 312493

## 68
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 68
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 8 MTR PSC POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 33 | 2017 | 66561 | 75471
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 33 | 262 | 8646 | 8731.8
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219 | 174.6
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43 | 90
[6 empty] | 262 | 264.6
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850 | 5389.44
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258 | 245
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145 | 137
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74 | 71
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292 | 255.24
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21 | 11
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180 | 174
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5 | 5
[6 empty] | 975 | 898.24
4 | 405000023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 424673 | 445906.65 | 450783.9
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150 | 3150
7 | 411000073 | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C x 70 sqmm AB Cable for Outdoor Termination application | NO | 6 | 3100 | 18600 | 2430
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900 | 1900
[6 empty] | 470096.65 | 458803.9
|  | COST OF MATERIALS |  |  |  | 551153.65 | 548396.14
9 |  | ADD:3% CONTINGENCIES |  |  |  | 16534.6095 | 16451.8842
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 11023.073 | 10967.9228
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11023.073 | 10967.9228
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 82673.0475 | 82259.421
|  | A |  |  |  | 672407.453 | 669043.2908
13 |  | CARTING OF PSC POLE AT | NO. | 33 | 246 | 8118 | 7260
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400 | 160
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575 | 550
16 |  | LABOUR CHARGES FOR | NO. | 33 | 757 | 24981 | 22275
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184 | 1890
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 33 | 419 | 13827 | 11550
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of HT AB Cable including fittings of All Accessories | KM | 1 | 28994 | 28994 | 11000
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 84433 | 60039
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 12664.95 | 9005.85
24 |  | B |  |  |  | 97097.95 | 69044.85
25 |  | A+B |  |  |  | 769505.403 | 738088.1408
|  | TOTAL ESTIMATE |  |  | Say Rs. | 769505 | 738088 | 31417

## 69
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 69
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 11 MTR RSJ POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE (116 X 110 X 11 Mtr) | NO. | 25 | 12986 | 324650
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 25 | 262 | 6550
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 | 405000023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 424673 | 445906.65
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C x 70 sqmm AB Cable for Outdoor Termination application | NO | 6 | 3100 | 18600
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
470096.65
|  | COST OF MATERIALS |  |  |  | 807146.65
9 |  | ADD:3% CONTINGENCIES |  |  |  | 24214.3995
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 16142.933
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 16142.933
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 121071.9975
|  | A |  |  |  | 984718.913
13 |  | CARTING OF RSJ POLE AT | NO. | 25 | 246 | 6150
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 25 | 1268 | 31700
ERECTION OF RSJ POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 25 | 419 | 10475
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of HT AB Cable including fittings of All Accessories | KM | 1 | 28994 | 28994
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 85832
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 12874.8
24 |  | B |  |  |  | 98706.8
25 |  | A+B |  |  |  | 1083425.713
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1083426

## 70
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM 70
RE/CITY COST DATA FOR THE YEAR 2019-20
11 KV LINE USING ABC OF SIZE 11 KV 3x 70 SQ MM ON 10 MTR PSC POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 30 | 3505 | 105150
2 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 6 | 975 | 5850
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 4 | 73 | 292
| 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 1 | 21 | 21
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
975
4 | 405000023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | 1.05 | 424673 | 445906.65
Special Accessories For AB Cable i.e.tension Clamp, Suspention Clamp & Insulated Mid Span Joint
5 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | 4 | 135 | 540
6 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | 21 | 150 | 3150
7 | 411000073 | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C x 70 sqmm AB Cable for Outdoor Termination application | NO | 6 | 3100 | 18600
8 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | 50 | 38 | 1900
470096.65
|  | COST OF MATERIALS |  |  |  | 588956.65
9 |  | ADD:3% CONTINGENCIES |  |  |  | 17668.6995
10 |  | ADD:2% STORAGE CHARGES |  |  |  | 11779.133
11 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11779.133
12 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 88343.4975
|  | A |  |  |  | 718527.113
13 |  | CARTING OF 10 mtr PSC POLE AT | NO. | 30 | 400 | 12000
DESTINATION
14 |  | SURVEY,TREE CUTTING &COMPENSATION |  |  | ----LS---- | 400
15 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ----LS---- | 575
16 |  | LABOUR CHARGES FOR | NO. | 30 | 1815 | 54450
ERECTION OF PSC POLE INCLUDING
DIGGING OF PITS, FIXING OF POLE
FIXTURE etc. AND PAINTING OF
STEEL FIXTURE.
17 |  | LABOUR CHARGES FOR FIXING GUYS | NO. | 6 | 364 | 2184
18 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT AND COAL
19 | 9903000006 | Stringing of HT AB Cable including fittings of All Accessories | KM | 1 | 28994 | 28994
20 | 9911000162 | Crimping Of Insulated Mid Span Joint For ABC | NO | 4 | 11 | 44
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.9 | 5900 | 5310
22 |  | LABOUR CHARGES… |  |  |  | 116527
23 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 17479.05
24 |  | B |  |  |  | 134006.05
25 |  | A+B |  |  |  | 852533.163
|  | TOTAL ESTIMATE |  |  | Say Rs. | 852533

## 71
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 71
RE/CITY COST DATA FOR THE YEAR 2019-20
SINGLE POLE STRUCTURE WITH 11 KV DO FUSE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 1 | 2017 | 2017
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 458 | 916
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 1500 MM FOR TOP FABRI. | No | 2 | 458 | 916
3 |  | CROSS ARM FOR MOUNTING DO Fuse | NO. | 1 | 719 | 719
| 36 11 00 0038 | M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | No | 1 | 719 | 719
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 65 | 260
| 26 01 00 0049 | Side clamp | No | 4 | 65 | 260
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  |  | NO | 1 | 5 | 5
1057
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 1 | 262 | 262
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 11650.62
|  | ADD:3% CONTINGENCIES |  |  |  | 349.5186
|  | ADD:2% STORAGE CHARGES |  |  |  | 233.0124
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 233.0124
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 1747.593
11 |  | A |  |  |  | 14213.7564
12 |  | (A) CARTING OF PSC POLE AT | NO. | 1 | 246 | 246
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 905 | 905
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 1 | 419 | 419
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 2 | 364 | 728
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
18 |  | LABOUR CHARGES |  |  |  | 6068
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 910.2
20 |  | B |  |  |  | 6978.2
21 |  | A+B |  |  |  | 21191.9564
|  | TOTAL ESTIMATE |  |  | Say Rs. | 21192

## 72
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 72
RE/CITY COST DATA FOR THE YEAR 2019-20
PROVIDING FANCING AROUND DIST. TRANSFORMER CENTRE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 09 00 0004 | MS PIPE OF SQUARE HOLLOW SECTION (SHS) | KG. | 62.475 | 54 | 3373.65 | 10.5 mtr | 62.475 | MS PIPE OF SQUARE HOLLOW SECTION (SHS)62.47549.5 mm X 49.5 mm X 4.5 mm62.475with conversion factor of 5.95 Kg/mtr
49.5 mm X 49.5 mm X 4.5 mm
with conversion factor of 5.95 Kg/mtr
2 |  | MS PIPE OF SQUARE HOLLOW SECTION (SHS) | KG | 117.18 | 50 | 5859 |  | 117.1764
|  | 32 mm X 32 mm X 3.2 mm |  |  |  |  | 43.56 mtr |  | 32 mm X 32 mm X 3.2 mm with conversion factor of 2.69 Kg/mtr
with conversion factor of 2.69 Kg/mtr
3 |  | M.S.Angle 25x25x3mm | KG | 70.72 | 47 | 3323.84 |  | 70.72
|  | with conversion factor of 1.6 Kg/mtr |  |  |  |  | 44.2 mtr |  | with conversion factor of 1.6 Kg/mtr
3.2 kg misc
1 kg hanger
4 |  | GI Wire 10 SWG for Chain Link (mesh of 2" x 2") | KG | 28.5 | 70 | 1995
|  | with conversion factor of 3 Kg/Sq. meter | [6 empty] | with conversion factor of 3 Kg/Sq. meter
5 |  | COST OF MATERIALS |  |  |  | 14551.49
6 |  | ADD:3% CONTINGENCIES |  |  |  | 436.5447
7 |  | ADD:2% STORAGE CHARGES |  |  |  | 291.0298
8 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 291.0298
9 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2182.7235
10 |  | A |  |  |  | 17752.8178
11 |  | LABOUR CHARGES FOR PROVIDING FANCING |  | 1 | 4700 | 4700
AROUND DIST. TRANSFORMER CENTER
12 |  | HINGERS, STOPPERS (Lum Sum) |  | 1 | 770 | 770
13 |  | LABOUR OF COLOUR WITH REDOXIDE AND COLOUR |  | 1 | 630 | 630
14 |  | CONCRETING OF RCC WITH MATERIAL(1:2:4) | CMT | 0.2565 | 5900 | 1513.35
15 |  | LABOUR CHARGES… |  |  |  | 7613.35
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1142.0025
17 |  | B |  |  |  | 8755.3525
18 |  | A+B |  |  |  | 26508.1703
|  | TOTAL ESTIMATE |  |  | Say Rs. | 26508
17752.6475
1643.7637

## 73
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 73
RE/CITY COST DATA FOR THE YEAR 2019-20
REPLACEMENT OF SINGLE PHASE SERVICE CONNECTION BY 4.0 MM2 TWIN CORE ARMOURD CABLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 16 07 00 0001 | PVC INSULATED PVC ARMOURD | MTR. | 30 | 31.32 | 939.6
4.o MM2TWIN CORE CABLE
2 | 01 03 00 0003 | G.I.WIRE NO.10 (3.15 MM) | KG. | 1.5 | 145 | 217.5
3 | 20 04 00 0001 | REEL INSULATOR | NO. | 30 | 0.55 | 16.5
4 | 20 05 00 0001 | EGG INSULATOR | NO. | 2 | 1.6 | 3.2
5 |  | COST OF MATERIALS |  |  |  | 1176.8
6 |  | ADD:3% CONTINGENCIES |  |  |  | 35.304
7 |  | ADD:2% STORAGE CHARGES |  |  |  | 23.536
8 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 23.536
9 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 176.52
10 |  | A |  |  |  | 1435.696
11 |  | LABOUR CHARGES FOR LAYING OF |  | 1 | 170 | 170
REPLACEMENT OF SERVICE CONNECTION
12 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 25.5
13 |  | B |  |  |  | 195.5
14 |  | A+B |  |  |  | 1631.196
|  | TOTAL ESTIMATE |  |  | Say Rs. | 1631
1520

## 74
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 74
RE/CITY COST DATA FOR THE YEAR 2019-20
REPLACEMENT OF SINGLE PHASE MMB BY SMC
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 16 07 00 0001 | Single Phase SMC meter Box | NO. | 1 | 219 | 219
2 |  | SUNDRY MATERIAL INCLUDING
COST OF SCREW,BOLTS,BLACK TAPS,
|  | BINDING WIRE ,EARTHING BOLTS ETC. WITH |  |  |  | 5.254
PREFORMED FITTING.
| 15 05 00 0044 | (a) Jasati Khila | KG | 0.0572 | 70 | 4.004
| 15 05 00 0013 | (b) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 1 | 0.55 | 0.55
| 13 01 00 0006 | (c) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 1 | 0.7 | 0.7
5.254
3 |  | COST OF MATERIALS |  |  |  | 224.254
4 |  | ADD:3% CONTINGENCIES |  |  |  | 6.7276
5 |  | ADD:2% STORAGE CHARGES |  |  |  | 4.4851
6 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4.4851
7 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 33.6381
8 |  | A |  |  |  | 273.5899
9 |  | Replacement of 1 Ph meter box without meter |  | 1 | 50 | 50
10 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7.5
11 |  | B |  |  |  | 57.5
12 |  | A+B |  |  |  | 331.0899
|  | TOTAL ESTIMATE |  |  | Say Rs. | 331

## 75
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 75
RE/CITY COST DATA FOR THE YEAR 2019-20
SINGLE PHASE METER REPLACEMENT (UP TO 6 KW LOAD )
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 1 | 465 | 465
2 |  | COST OF MATERIALS |  |  |  | 465
3 |  | ADD:3% CONTINGENCIES |  |  |  | 13.95
4 |  | ADD:2% STORAGE CHARGES |  |  |  | 9.3
5 |  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 9.3
6 |  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 69.75
7 |  | A |  |  |  | 567.3
8 |  | Replacement of 1 Ph meter only (Rural Area) by another one. |  | 1 | 45 | 45
9 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 6.75
10 |  | B |  |  |  | 51.75
11 |  | A+B |  |  |  | 619.05
12 |  | TOTAL ESTIMATE |  |  | Say Rs. | 619
725
-106

## Material (hidden)
Material Procurement Cost for preparation of COST DATA for the year 2019-20
Sr. No | Item Code | Name | Unit | 2012-13 | 2014-15 | 2015-16 | 2019-20 | Diff | % Rise
1 | 36 04 00 0036 | RSJ POLE 116*110*11MTR | NO. | 10857 | 12878 | 11360 | 12986 | 1626 | 14.31% |  | 12986.49 | 12986
2 | 26 11 00 0003 | RSJ POLE 116*100*9 MTR | NO. | 8930 | 10536 | 9232 | 10478 | 1246 | 13.5% |  | 10478.34
3 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2010 | 2345 | 2287 | 2017 | -270 | -11.81% |  | 2023.7
4 | 26 11 00 0003 | PSC POLE 10 MTR | NO. | 2990 | 3900 | 3548 | 3505 | -43 | -1.212% |  | 3540
5 | 36 04 00 0037 | RSJ POLE 150*150*13MTR | NO. |  | 22220 | 20016 | 17047 | -2969 | -14.83% |  | 17043 | 17047
6 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 100MM2 DOG | KM. | 49310 | 50245.51 | 55910 | 58038 | 2128 | 3.806% |  | 58038.3
7 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55 MM2 WEASEL | KM | 27045 | 27546.48 | 29750 | 31288 | 1538 | 5.17% |  | 31287.7
8 | 01 02 00 0031 | AL.ALLOY CONDUCTOR 34 MM2 RABIT | KM | 17050 | 17379.73 | 18806 | 19989 | 1183 | 6.291% |  | 19989
9 |  | -DO- BUT 34MM2 AAA CONDUCTOR | KM. | 17050 | 17380 | 18806 | 19989 | 1183 | 6.291% |  | 19989
10 | 26 09 00 0014 | C TYPE FORMATION | NO | 475 | 540 | 550 | 672 | 122 | 22.18% |  |  | 672
11 | 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 230 | 264 | 245 | 258 | 13 | 5.306% |  | 258
12 | 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 125 | 148 | 137 | 145 | 8 | 5.839% |  | 145
13 | 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 65 | 76 | 71 | 74 | 3 | 4.225% |  | 74
14 | 01 03 00 0012 | (d) Stay wire- 7/12 5 Kg. | KG | 57.39 | 67.15 | 63.81 | 73 | 9.19 | 14.4% |  | 72.688
15 | 20 03 00 0001 | (e) LT Guy Insulator - 1 No. | NO. | 11 | 11 | 11 | 21 | 10 | 90.91% |  | 21.24
16 | 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 21 | 23.12 | 28 | 30 | 2 | 7.143% |  | 30.27
17 | 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 144 | 186 | 174 | 180 | 6 | 3.448% |  | 190
18 | 26 14 0000 17 | (g) Thimble for HT/LT Line | NO | 5 | 5 | 5 | 5 | 0 | 0% |  | 5
19 | 20 02 00 0001 | (a) LT Shackle Insulator | No | 8.5 | 10.64 | 16.91 | 14 | -2.91 | -17.21% |  | 13.57
20 | 20 10 00 0002 | (b) LT Shackle Bolt | No | 8.4 | 8.4 | 8.4 | 11 | 2.6 | 30.95% |  | 11.33
21 | 26 01 00 0040 | (c) U clamp | No | 48 | 57 | 54 | 56 | 2 | 3.704% |  | 56
22 | 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 75 | 85 | 75 | 70 | -5 | -6.667% |  | 73.986
23 | 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 75 | 85 | 75 | 70 | -5 | -6.667% |  | 72.806
24 | 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 75 | 85 | 75 | 70 | -5 | -6.667% |  | 72.806
25 | 04 15 00 0019 | (d) P.G. Clamp for Weasle or Rabbit | No | 68 | 76 | 70 | 110 | 40 | 57.14%
26 | 01 01 00 0003 | (c) Alu. Binding wire | KG | 160 | 165 | 100 | 120 | 20 | 20%
27 | 19 05 00 0006 | (d) HT Tape for binding | Mtr | 2 | 2.5 | 2.5 | 13 | 10.5 | 420%
28 | 26 15 00 0024 | (d) Line spacers for 5 wire line | NO | 39 | 43 | 43 | 55 | 12 | 27.91%
29 | 26 15 00 0003 | (d) Line spacers for 4 wire line | NO | 29 | 33 | 33 | 45 | 12 | 36.36%
30 | 26 15 00 0022 | (d) Line spacers for 3 wire line | NO | 23 | 27 | 27 | 30 | 3 | 11.11%
31 | 26 15 00 0001/2 | (d) Line spacers for 2 wire line | NO | 16 | 20 | 20 | 20 | 0 | 0%
32 |  | ANGLE TAPPING FOR 22KV | No |  | 414 | 414 | 458 | 44 | 10.63% |  |  | 458
33 | 26 17 00 0005 | (a) M.S. Channel 100x50x6mm - 150mm for horizontal cross arm(Packing Piece) | NO | 56 | 73 | 76 | 81 | 5 | 6.579% |  | 81
34 | 26 09 00 0053 | (b) M.S. Channel 100x50x6mm - 1500mm for horizontal cross arm | NO | 575 | 723 | 665 | 719 | 54 | 8.12% |  | 719
35 | 26 09 00 0047 | (c) M.S. Channel 100x50x6mm - 1000mm for mounting trans. | NO | 382 | 466 | 493 | 533 | 40 | 8.114% |  | 533
36 | 26 09 00 0004 | (d) M.S. Angle 50x50x6mm - 800mm for mounting trans. | NO | 60 | 73 | 174 | 185 | 11 | 6.322%
37 | 26 09 00 0046 | (e) M.S. Channel 100x50x6mm - 900mm for fixing HG Fuse | NO | 385 | 436 | 396 | 428 | 32 | 8.081%
38 | 26 09 00 0003 | (f) M.S. Angle 50x50x6mm - 400mm for fixing HG Fuse. | NO | 130 | 150 | 95 | 100 | 5 | 5.263% |  | 100
39 | 36 11 00 0037 | (d) M.S. Angle Fab. 65x65x6mm -750mm for side arms for HG fuse | NO | 195 | 225 | 203 | 224 | 21 | 10.34% |  | 224
40 | 21 07 00 0048 | M.S.Angle 65x65x6mm - 1 Mtr for angle support for | NO | 260 | 300 | 270 | 298 | 28 | 10.37% |  | 298
41 | 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 1326 | 1538 | 1413 | 1530 | 117 | 8.28% |  | 1530
42 | 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 2750 mm | NO | 1115 | 1294 | 1190 | 1287 | 97 | 8.151% |  | 1287
43 | 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 728 | 840 | 756 | 834 | 78 | 10.32% |  | 797
44 | 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 728 | 840 | 756 | 834 | 78 | 10.32% |  | 797
45 | 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 210 | 243 | 218 | 241 | 23 | 10.55% |  | 224
46 | 36 11 00 0031 | Angle Bracing for D.P-65x65x6-750MM | NO. | 195 | 225 | 203 | 224 | 21 | 10.34% |  | 224
47 | 26 09 00 0029/31 | M.S.Angle 65x65x6mm - 2 Mtr for Guarding Angle cross arm/Guarding channel | No | 528 | 610 | 551 | 607 | 56 | 10.16% |  | 607
48 |  | M.S Angle Tapping-22KV FEBRI. 65x65x6x1150MM | NO. | 298 | 343 | 309 | 341 | 32 | 10.36% |  | 341
49 | 21 07 00 0060 | HOOK CLAMP FOR FIXING (DISTRIBUTION CLAMP) | NO. | 50 | 60 | 60 | 60 | 0 | 0% |  | 65
50 | 26 09 00 0034 | V CROSS ARMS 11KV | NO. | 484 | 559 | 503 | 555 | 52 | 10.34% |  | 555
51 | 27 09 00 0034 | V CROSS ARMS 22KV | NO. | 628 | 725 | 653 | 720 | 67 | 10.26% |  | 720
52 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 105 | 123 | 120 | 123 | 3 | 2.5% |  | 123
53 | 06 13 00 0003 | 22 KV A.B. SWITCH 400 AMP. | SET | 16156 | 16156 | 16156 | 19373 | 3217 | 19.91% |  | 19372.5 | 19373
54 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 5428.5 | 5830 | 7000 | 7658 | 658 | 9.4% |  | 7658.2 | 7658
55 | 13 05 00 0001 | 22 KV.H.G. FUSES. | NO | 2600 | 2600 | 2600 |  | -2600 | -100%
56 | 13 05 00 0001 | 11 KV.H.G. FUSES.(Now DO fuse) | NO | 987 | 987 | 987 | 846.06 | -140.94 | -14.28%
57 | 22 01 00 0004 | 22 KV DIST.TYPE LIGHTENING ARRESTOR | NO | 1260 | 1260 | 1260 |  | -1260 | -100%
58 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO | 356.76 | 356.76 | 339 | 309 | -30 | -8.85%
59 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO | 60 | 60 | 60 | 60 | 0 | 0%
60
61 | 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 276.15 | 281.24 | 281.24 | 313 | 31.76 | 11.29% |  | 313 | 313
62 | 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 72.45 | 90.3 | 90 | 43 | -47 | -52.22% |  | 42.71
63 | 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 54.07 | 61.15 | 58.2 | 73 | 14.8 | 25.43% |  | 73.22
64 | 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 8 | 8.9 | 8.5 | 9 | 0.5 | 5.882% |  | 39.53
65 | 01 03 00 0070 | Bar bed wire - 1.591 Kg for 1 No. anticlaimbing device | NO. | 63 | 104 | 100 | 120 | 20 | 20%
66 | 21 04 00 0002 | L.T. DIST. BOX -25 KVA | NO. | 5103 | 5103.5 | 5103 | 6900 | 1797 | 35.21% |  | 6900
67 | 21 04 00 0006 | L.T. DIST. BOX -63 KVA | NO. | 5775 | 6046.95 | 5948 | 6993 | 1045 | 17.57% |  | 6993
68 | 21 04 00 0009 | L.T. DIST. BOX -100 KVA | NO. | 8127 | 8338.68 | 8770 | 8563 | -207 | -2.36% |  | 8562.75
69 | 21 04 00 0009 | L.T. DIST. BOX -200 KVA | NO. | 88044.1 | 88044.1 | 91193 | 82156 | -9037 | -9.91% |  | 82155.94
70 | 21 04 00 0009 | L.T. DIST. BOX -500 KVA | NO. | 167990.24 | 167990.24 | 167990 | 183748 | 15758 | 9.38% |  | 183748.16
71 | 1601000073 | (i) 10-60 A Static Meter | NO | 2249.62 | 2024.34 | 1884 | 1472 | -412 | -21.87% |  | 1472
72 | 1607000009 | (ii) 3-ph SMB | NO | 631.06 | 542.69 | 583 | 527 | -56 | -9.605% |  | 527.46
73 | 1601000070 | (i) 200/5 A Static Meter. | NO | 2540 | 2540 | 2162 | 1589 | -573 | -26.5% |  | 1589.46
74 | 1608000047 | (iv) Ring Type LT CT-200/5A | SET | 298.73 | 298.73 | 470 | 389 | -81 | -17.23% |  | 388.5
75 | 1601000069 | (i) 100/5 A Static Meter . | NO | 2539.92 | 2540 | 2162 | 1589 | -573 | -26.5% |  | 1589.46
76 | 1608000046 | (iv) Ring Type LT CT-100/5 A | SET | 948.36 | 948.36 | 820.58 | 735 | -85.58 | -10.43% |  | 735
77 | 1608000049 | (iv) Ring Type LT CT-900/5A | SET | 1955 | 1955 | 1955 | 560 | -1395 | -71.36% |  |  | 560
78 | 13 02 00 0004 | (c) Fuse element-3 & 5 Amp | NO. | 14 | 15 | 15 | 14 | -1 | -6.667%
79 | 13 02 00 0004 | (c) Fuse element-10 Amp | NO. | 15 | 16 | 16 | 14 | -2 | -12.5%
80 | 13 02 00 0004 | (c) Fuse element-20 Amp | NO. | 15 | 16 | 16 | 18 | 2 | 12.5%
81 | 13 01 00 0006 | (b) Tinned Copper Fuse Wire No.18(for 16 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.6 | 0.7 | 0.1 | 16.67% |  |  | 0.7
82 | 13 01 00 0015 | (d) Tinned Copper Fuse Wire No.14(for 63/32 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.6 | 0.7 | 0.1 | 16.67% |  |  | 0.7
83 | 13 01 00 0017 | (f) Tinned Copper Fuse Wire No.12(for 100 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.6 | 0.7 | 0.1 | 16.67% |  |  | 0.7
84 | 14 01 00 0017 | (f) Tinned Copper Fuse Wire No.10(for 200 Amp. Fuse) | Grams | 0.5 | 0.6 | 0.6 | 0.7 | 0.1 | 16.67% |  |  | 0.7
85 | 04 16 00 0004 | (h)Alu.lugs for kit-Kat /Trans. LT 10 SQ.MM Cable | NO. | 2.5 | 2.7 | 2.7 | 1.77 | -0.93 | -34.44%
86 | 26 01 00 0049 | (k)Alu.lugs for kit-Kat/Trans. LT 16 SQ.MM Cable | NO. | 2.5 | 2.7 | 2.7 | 2.7 | 0 | 0%
87 | 26 01 00 0049 | (k) Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 3 | 3.25 | 3.25 | 3.2 | -0.05 | -1.538%
88 | 26 01 00 0049 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 3.5 | 3.75 | 3.75 | 3.54 | -0.21 | -5.6%
89 | 26 01 00 0049 | (j) Alu.lugs for kit-Kat 50 SQ.MM Cable | NO. | 5.1 | 5.5 | 4.6 | 5.5 | 0.9 | 19.57%
90 | 26 01 00 0049 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 7.6 | 8.2 | 5.1 | 8.9 | 3.8 | 74.51%
91 | 26 13 00 0002 | (h)Alu.lugs -Trans. LT 150 SQ.MM Cable | NO. | 15.5 | 16.5 | 14.5 | 18.5 | 4 | 27.59%
92 | 26 13 00 0002 | (I) Three hole patties | NO. | 20 | 22 | 20 | 30 | 10 | 50%
93 | 26 01 00 0049 | (i) Side Clamp | NO. | 57 | 67 | 63 | 65 | 2 | 3.175%
94 |  | 11KV SDT/SPT 24 A capacity | No | 22939 | 112000 | 112000 | 112000 | 0 | 0% |  | 190634.9
95 |  | 11KV SDT/SPT 30 A capacity | No | 22939 | 135000 | 135000 | 135000 | 0 | 0%
96 |  | 11KV SDT/PAT 24.7 A capacity | No | 22939 | 190635 | 190635 | 190635 | 0 | 0%
97 |  | 11KV SDT/PAT 54 A capacity | No | 22939 | 278298 | 278298 | 278298 | 0 | 0% |  | 278298.3
98 |  | Gang operated three pole double throw change over switch | Set | 1 | 7500 | 7500 | 7611 | 111 | 1.48% |  |  | 7611 |  | 6450 | 7611
99 |  | (e) C.I. Earthing pipe 100 mm dia,13 mm thick | No. | 2 | 5600 | 5600 | 6136 | 536 | 9.571% |  |  |  |  | 5521 | 6514.78
100 |  | (f) GI Earthing strip (50x6mm) | Kg. | 50 | 30 | 30 | 68 | 38 | 126.7% |  |  |  |  | 5200 | 6136
101 |  | (a) IDMT RELAY | No. | 1 | 4500 | 4500 | 6515 | 2015 | 44.78% |  |  | c&s, stelmac |  | 57.42 | 67.7556
102 |  | (b) HT 11KV C T coil (30/1, 15 VA) | No. | 1 | 10920 | 10920 | 10920 | 0 | 0%
103 |  | (c) 2C X 2.5 sq. mm armoured cu cable for control wiring | Mtr. | 70 | 70 | 70 | 61 | -9 | -12.86%
104 |  | (d) Relay MS box including connectors and wiring material. | LS | 1 | 1000 | 1000 | 527 | -473 | -47.3%
105 |  | X'MER 05 KVA 11KV/0.433KV. | No | 22939 | 20772.36 | 30745 | 37400 | 6655 | 21.65% |  | 37400
106 | 44 06 02 0002 | X'MER 10 KVA 11KV/0.433KV. | NO. | 35885.62 | 35033.57 | 35195 | 32008 | -3187 | -9.055% |  | 32007.5
107 | 44 06 02 0002 | X'MER 16 KVA 11KV/0.433KV. 3 Star | NO. | 46122.03 | 40991.45 | 38742 | 43400 | 4658 | 12.02% |  | 43400
108 | 44 06 02 0002 | X'MER 16 KVA 11KV/0.433KV. 4 Star | NO. | 49450 | 45954.6 | 47744 | 43400 | -4344 | -9.099% |  | 43400
109 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV. 3 Star | NO. | 59111.04 | 48428.07 | 48355 | 55350 | 6995 | 14.47% |  | 55350
110 | 44 06 02 0002 | X'MER 25 KVA 11KV/0.433KV. 4 Star | NO. | 63012.6 | 58281.13 | 60172 | 55350 | -4822 | -8.014% |  | 55350
111 | 44 06 02 0001 | X'MER 63 KVA 22 KV/0.433KV. 4 Star | NO. | 134644.57 | 134644.57 | 121000 | 95000 | -26000 | -21.49% |  | 95000
112 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV. 3 Star | NO. | 100131.7 | 83170.32 | 79036 | 95000 | 15964 | 20.2% |  | 95000
113 | 44 06 02 0001 | X'MER 63 KVA 11KV/0.433KV. 4 Star | NO. | 100131.7 | 100131.7 | 88989 | 95000 | 6011 | 6.755% |  | 95000
114 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. 3 Star | NO. | 133585 | 105881.32 | 104475 | 124200 | 19725 | 18.88% |  | 124200
115 | 44 06 02 0023 | X'MER 100 KVA 11KV/0.433KV. 4 Star | NO. | 133585 | 133585 | 111904 | 124200 | 12296 | 10.99% |  | 124200
116 | 44 06 02 0023 | X'MER 100 KVA 22KV/0.433KV. 4 Star | NO. | 176211.57 | 176211.57 | 180602 | 124200 | -56402 | -31.23% |  | 124200
117 | 44 06 02 0023 | X'MER 500 KVA 11KV/0.433KV. | NO. | 624750 | 624750 | 581066 | 849000 | 267934 | 46.11% |  | 849000
118 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV. 3 Star | NO. | 246787.5 | 222764.93 | 202947 | 249500 | 46553 | 22.94% |  | 249500
119 | 44 06 02 0023 | X'MER 200 KVA 11KV/0.433KV. 4 Star | NO. | 246787.5 | 244067.34 | 244229 | 249500 | 5271 | 2.158% |  | 249500
120 | 614000011 | 11 KV R M U(SF-6) | NO | 360640 | 360640 | 400000 | 435115 | 35115 | 8.779%
121 | 04 05 01 0004 | 3x 35 Sq.mm(P) +1x16 sq.mm.(N) +1x25 sq.mm. bare messenger Aerial Bunched cable | KM | New | 85551.86 | 89796 | 89796 | 0 | 0% | 85304/AT ON DTD 28.9.16 | 125513.28 |  | 3x 35 Sq.mm +1x50 sq.mm. +1x25 sq.mm. bare messenger Aerial Bunched cable
122 | New Item | 3x 50 Sq.mm(P) +1x25 sq.mm.(N) +1x35 sq.mm. bare messenger Aerial Bunched cable |  |  |  |  | 125513
123 | 405000019 | 1Cx 35 Sq.mm+35mm Aerial Bunched cable | KM | New | 35650.98 | 39900 | 44527 | 4627 | 11.6% |  | 44526.56
124 | 04 05 01 0023 | 11 KV 3x 70 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | New | 352754.48 | 429318 | 424673 | -4645 | -1.082%
125 | to be deleaded | 12 KV 3x 120 sq.mm. + 1x 70 sq.mm. bare messenger Aerial Bunched cable | KM | New | 530185.21 | 593218 |  | -593218 | -100%
126 | 2601000137 | Self tightening anchoring (Dead end) clamp with pole bracket using Stainless Steel Strap & Buckle | NO | New | 135 | 135 | 135 | 0 | 0% |  |  | 135
127 | 2601000136 | Self locking Suspension Clamp witth pole bracket using Stainless Steel Strap & Buckle | NO | New | 150 | 150 | 150 | 0 | 0%
128 | 411000073 | Pre Insulated mid span joints for phase & neutral for 16 sq mm to50mm2 | NO | New | 135 | 135 | 135 | 0 | 0%
129 | 2601000138 | Stainless Steel of Size Strap 20mm*0.7mm & Buckle width 20 mm | NO | New | 38.01 | 38 | 38 | 0 | 0%
130 | New Item | Providing & fixing Heat Shrinkable type Cable Jointing kit suitable for 11 KV 3C AB Cable for Outdoor Termination application | NO |  |  |  | 3100
131 | 13 03 00 0004 | KIT-KAT FUSE 16 AMPS. | NO. | 35.25 | 39.3 | 39.3 | 40 | 0.7 | 1.781% |  |  | 40
132 | 15 05 00 0013 | (a) Screw- 19x8 ( for 16 Amp Fuse )/Screw 20x8 | NO | 0.48 | 0.55 | 0.55 | 0.55 | 0 | 0%
133 | 13 03 00 0006 | KIT-KAT FUSE 32 AMPS. | NO. | 50.02 | 50.02 | 50.2 | 60 | 9.8 | 19.52% |  |  | 60
134 | 15 05 00 0012 | (e) Screw - 25x8 ( for 32 Amp Fuse) | NO | 0.6 | 0.7 | 0.7 | 0.7 | 0 | 0%
135 | 13 03 00 0014 | KIT-KAT FUSE 100 AMPS. | NO. | 193.55 | 183.55 | 189 | 228 | 39 | 20.63% |  | 227.84
136 | 15 05 00 0028 | (e) Screw - 75x8 ( for 100 Amp Fuse) | NO | 1.2 | 1.35 | 1.35 | 1.35 | 0 | 0%
137 | 13 03 00 0020 | KIT-KAT FUSE 200 AMPS. | NO. | 538.2 | 505.05 | 525 | 582 | 57 | 10.86% |  | 582.4
138 | 15 05 00 0028 | (e)Bolt type Screw - 1/8 x.2" ( for 200 Amp Fuse) | NO | 2 | 2.3 | 2.3 | 2.3 | 0 | 0%
139 | 30 06 00 0007 | STREET LIGHT FIXURE COMPLETE WITH HOLDER | NO. | 400 | 450 | 525 | 575 | 50 | 9.524%
140 | 19 01 00 0005 | PVC INSULATED PVC SHETHED 2.5 MM2 TWIN CORE CABLE | MTR. | 5.2 | 5.42 | 5.73 | 6.85 | 1.12 | 19.55%
141 | 04 05 00 0009 | 11 KVXLPE CABLE 3 CORE 185 mm2 SIZE.(Double CKT) | MTR | 655 | 655 | 701 | 1034 | 333 | 47.5% |  | 1034.4235 | 1034
142 | 0405000009 | 11KV 240 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 754.3 | 754.3 | 861 | 1162 | 301 | 34.96% |  | 1162.3
143 | 04 01 00 0003 | 3.5 CORE PVC INSULATED & SHEATHED 150 MM2 | MTR | 301.7 | 358.26 | 345.7 | 363.44 | 17.74 | 5.132%
144 | 04 01 00 0004 | 3.5 CORE 70MM2 PVC CABLE. | MTR | 162 | 173.17 | 170.75 | 184.08 | 13.33 | 7.807%
145 | 04 01 00 0003 | 3.5 CORE 50MM2 PVC CABLE. | MTR | 109.16 | 127.26 | 134.05 | 137.82 | 3.77 | 2.812%
146 | 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 65.27 | 75.586 | 82.12 | 82.83 | 0.71 | 0.8646%
147 | 04 01 00 0035 | 4 C x 16mm2 LT PVC Cable | MTR | 50.72 | 52.28 | 56.25 | 61.304 | 5.054 | 8.985%
148 | 04 01 00 0034 | PVC ALUM.4 CX 10 MM2 UN-ARMOURED CABLE | MTR | 35.18 | 35.857 | 39.18 | 41.65 | 2.47 | 6.304%
149 | 04 01 00 0033 | PVC ALUM.4 CX6MM2 UN-ARMOURED CABLE | MTR | 20.7 | 21.17 | 23.32 | 26.96 | 3.64 | 15.61%
150 | 16 01 00 0008 | 1 PHASE ENERGY METER 5/20 AMPS. | NO. | 834.2 | 779.06 | 663 | 465 | -198 | -29.86% |  | 465
151 | 21 05 00 0002 | ICDP SWITCH 32 AMPS./30 AMPS. | NO. | 70 | 70 | 70 | 140 | 70 | 100% |  |  | 140
152 | 16 07 00 0003 | single phase SMC meter box | NO. | 193.37 | 201.6 | 231 | 219 | -12 | -5.195% |  | 218.5
153 | 16 07 00 0009 | Three phase SMC meter box for C.T. Operated meter | NO. | 993.6 | 907.2 | 919 | 882 | -37 | -4.026%
154 |  | PVC INSULATED PVC ARMOURD 4.o MM2 TWIN CORE CABLE | MTR. | 20 | 61 | 61 | 31.32 | -29.68 | -48.66%
155 | New added | PVC INSULATED PVC ARMOURD 2.5 MM2 TWIN CORE CABLE | MTR. |  |  |  | 27.263 | 27.263 | #DIV/0!
156 | 15 05 00 0044 | (a) Jasati Khila | KG | 70 | 80 | 80 | 70 | -10 | -12.5%
157 | 01 03 00 0003 | G.I.WIRE NO.10 (3.15 MM) | KG. | 54.07 | 61.15 | 58.43 | 70 | 11.57 | 19.8% |  | 69.6802
158 | 01 03 00 0002 | G.I.WIRE NO.8 (4 MM) | KG | 54.07 | 61.15 | 58.2 | 73 | 14.8 | 25.43% |  | 73.2202
159 | 20 04 00 0001 | REEL INSULATOR | NO. | 0.5 | 0.6 | 0.6 | 0.55 | -0.05 | -8.333%
160 | 20 05 00 0001 | EGG INSULATOR | NO. | 1.75 | 2 | 2 | 1.6 | -0.4 | -20%
161 | 19 05 00 0002 | (c) LT Tape | Mtr | 1.5 | 1.75 | 1.75 | 1.4769 | -0.27308 | -15.6%
162 | 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 258.59 | 223.46 | 170 | 164 | -6 | -3.529% |  | 163.96
163 | 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 134.6 | 143.7 | 138.8 | 128 | -10.8 | -7.781% |  | 127.72
164 | 26 01 00 0069 | Guy clamp for two way strain clamp (Stay Pair) | No | 144 | 186 | 174 | 180 | 6 | 3.448% |  |  | 180
165 | 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 157.7 | 165.28 | 192.6 |  | -192.6 | -100%
166 | 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 140 | 171.96 | 168.63 |  | -168.63 | -100%
167 | 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 40.74 | 46.49 | 67.8 | 219 | 151.2 | 223% |  | 219.48
168 | 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 47.88 | 61.66 | 57.06 |  | -57.06 | -100%
169 | 04 09 00 0025 | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 200 | 225 | 225 | 175 | -50 | -22.22% |  |  | 175
170 | 04 19 00 0010 | Doble Compressed 25 mm2 Cable Gland | No. | 130 | 140 | 140 | 135 | -5 | -3.571%
171 | 16 08 00 0010 | Test Terminal Box | No. | 800 | 875 | 875 | 875 | 0 | 0%
172 | New Item | 3 PH HT Connection SMC Box | No. |  |  |  | 2714 | 2714 | #DIV/0! | to be add in ht items
173 | New Item | 2C 4MM2 PVC CABLE | MTR |  |  |  | 9.35

## Annexure-F
UTTAR GUJARAT VIJ COMPANY LIMITED
ITEM WISE COST DATA FOR H.T.POWER SUPPLY FOR FY 2019-20
ANNEXURE-F
SR NO. | ITEM CODE | ITEM NO. | PARTICULARS | PARTICULARS | UNIT | RATE OF 2012-13 | RATE OF 2014-15 | RATE OF 2015-16 | RATE (In Rs.) | % Diff.
1 | 2 | 3 |  | 4 | 5 |  |  |  | 6
1 | 9603000051 | ITEM 1 | 0611000033 | 11KV INDOOR FEEDER BREAKER PANEL (VCB) COMPLETE IN ALL RESPECT AT S/S END | No. | 245668 | 237063 | 297000 | 451052 | 51.8694
2 | 9603000016 | ITEM 2 |  | 11KV DP STRUCTURE AT S/S END FOR O/H LINE AND U/G CABLE USING 11 MTR RSJ POLES | No. | 66420.4852 | 78167.1172 | 75548.932 | 82854.4768 | 9.67
3 | 9603000046 | ITEM 3 | 0405000009 | 11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH | Mtr. | 1052.1 | 1121.1 | 1205.97 | 1646.73 | 36.5482
4 | 9603000047 | ITEM 4 | 0405000010 | 11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH | Mtr. | 1173.246 | 1242.246 | 1401.17 | 1802.89 | 28.6703
5 | NEW | ITEM 5 |  | 11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD | Mtr. |  |  |  | 2813.98
6 |  | ITEM 6 |  | 11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD | Mtr. |  |  |  | 3073.64
7 | 9603000001 | ITEM 7 |  | 11KV TAPPING FROM EXISTING POLE | No. | 5492.8508 | 6191.6175 | 5881.0782 | 6498.18 | 10.493
8 | 9603000002 | ITEM 8 |  | 11KV D. P. STRUCTURE WITH A. B. SWITCH USING 8 MTR PSC POLES. | No. | 31405.8152 | 36033.4172 | 36743.722 | 38928.5868 | 5.9462
9 | 9603000057 | ITEM 9 |  | 11KV D. P. STRUCTURE WITH H.G. FUSE USING 8 MTR PSC POLES (WITHOUT AB SWITCH) | No. | 27824.5052 | 31884.1972 | 31223.222 | 31950.4064 | 2.329
10 | 9603000003 | ITEM 10 |  | 11KV D. P. STRUCTURE A. B. SWITCH USING 9 MTR RSJ POLES. | No. | 56389.6452 | 66303.8372 | 64822.692 | 70233.3268 | 8.3468
11 | 9603000060 | ITEM 11 |  | 11KV D. P. STRUCTURE WITH H.G. FUSE USING 9 MTR RSJ POLES. | No. | 45140.5552 | 52422.2372 | 48772.772 | 53075.9464 | 8.8229
12 | 9603000004 | ITEM 12 |  | 11KV D. P. STRUCTURE A. B. SWITCH USING 11 MTR RSJ POLES. | No. | 61091.5252 | 72018.3172 | 70015.012 | 76749.5968 | 9.6188
13 | 9603000059 | ITEM 13 |  | 11KV D. P. STRUCTURE H.G.FUSE USING 11 MTR RSJ POLES. | No. | 49842.4352 | 58136.7172 | 53965.092 | 59195.4664 | 9.6921
14 | 9603000005 | ITEM 14 |  | 11KV LINE WITH 55MM2 AAA CONDUCTOR USING 8 MTR/ 200 KG PSC POLES. WPZ - 100 KG/M2(SPAN 50 MTRS.) | KM | 219679.7786 | 243382.4825 | 251401.406 | 264765.2664 | 5.3157
15 | 9603000006 | ITEM 15 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-33 MTR) | KM | 718724.4502 | 846156.9185 | 813861.008 | 903056.7624 | 10.9596
16 | 9603000061 | ITEM 16 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-50 MTR) | KM | 524021.9062 | 610866.1785 | 591576.812 | 653787.6624 | 10.5161
17 | 9603000062 | ITEM 17 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE- 9 MTR (SPAN-50 MTR) | KM | 477003.1062 | 553721.3785 | 539653.612 | 592592.4624 | 9.8098
18 | 9603000050 | ITEM 18 |  | 11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON PSC POLE(SPAN-33 MTR) | KM | 282727.3772 | 317208.8437 | 324355.211 | 341478.7084 | 5.2792
19 | 9603000008 | ITEM 19 |  | 11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (33 MTR. SPAN) | KM | 842132.1964 | 974192.3126 | 954040.502 | 996865.6824 | 4.4888
20 | 9603000009 | ITEM 20 |  | 11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (50 MTR SPAN) | KM | 633394.2844 | 723279.8386 | 716590.364 | 747918.6624 | 4.3719
21 | 9603000010 | ITEM 21 |  | 11KV RAILWAY CROSSING BY 185 MM2 U/G XLPE CABLE. ( DOUBLE CKT 115 MTR LENGTH) | NO. | 644430.5248 | 653229.8646 | 663160.882 | 775184.03 | 16.8923
19 | 9603000011 | ITEM 22 |  | GUARDING FOR H.T./ L.T.LINES AND P&T LINES | Mtr. | 6120.7864 | 7392.228 | 7517.8652 | 8237.94 | 9.5782
20 | 9603000012 | ITEM 23 |  | 11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 8 MTR PSC POLES | No. | 52597.0608 | 61529.9736 | 61659.3114 | 65320.6112 | 5.938
21 | 9603000013 | ITEM 24 |  | 11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 11 MTR RSJ POLES | No. | 75247.1608 | 87292.3336 | 84000.0714 | 92457.9012 | 10.0688
22 | 9603000063 | ITEM 25 |  | 11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 9 MTR RSJ POLES | No. | 68218.0088 | 79240.0896 | 76465.3514 | 84036.2412 | 9.9011
23 | 9603000049 | ITEM 26 |  | RIVER CROSSING USING 10 MTR PSC POLES FOR 11KV | No. | 60449.3332 | 72963.5788 | 70482.5572 | 73937.942 | 4.9025
24 | 9603000015 | ITEM 27 |  | RIVER CROSSING USING 11 MTR RSJ POLES FOR 11KV | No. | 109171.8932 | 129970.8988 | 123089.8572 | 134274.082 | 9.0862
SUB TOTAL OF COLUMN NO.6 ( I.E. ITEM 1 TO ITEM 27 )
26 |  | ITEM 28 |  | SERVICE CONNECTION CHARGES
27 |  |  |  | 1) Up to 500 KVA | No. | 9000 | 9000 | 9000 | 9000 | 0
28 |  |  |  | 2) 500 KVA to 1000 KVA | No. | 9000 Plus 1400 per 100 KVA above 500KVA | 9000 Plus 1400 per 100 KVA above 500KVA | 9000 Plus 1400 per 100 KVA above 500KVA | 9000 Plus 1400 per 100 KVA above 500KVA | 0
29 |  |  |  | 3) Above 1000 KVA | No. | 16000 Plus 1700 per 100 KVA above 1000KVA | 16000 Plus 1700 per 100 KVA above 1000KVA | 16000 Plus 1700 per 100 KVA above 1000KVA | 16000 Plus 1700 per 100 KVA above 1000KVA | 0
TOTAL COST TO BE BORNE BY APPLICANT (SUBTOTAL FROM ITEM 21 TO ITEM 27 AND ITEM 28)
30 | 9603000017 | ITEM 29 | 1605000007 | 1)COST OF TVM - 5 Amp Sec | No. | 8312.9 | 8312.9 | 8312.9 | 5599 | -32.6469
31 | 9603000018 | ITEM 30 | 1605000008 | 2)COST OF TVM - 1 Amp Sec | No. | 19275.83 | 19275.83 | 19275.83 | 26054.06 | 35.1644
32 | 9603000019 | ITEM 31 | 4456000030 | 1)COST OF 11 KV CTPT SET 10/5 A | No. | 37769.55 | 41872.64 | 42113 | 25783 | -38.7766
33 | 9603000020 | ITEM 32 | 4456000031 | 2)COST OF 11 KV CTPT SET 15/5 A | No. | 35215.86 | 37578.8 | 37796 | 24249 | -35.8424
34 | 9603000021 | ITEM 33 | 4456000034 | 3)COST OF 11 KV CTPT SET 20/5 A | No. | 31056.15 | 37497.34 | 36438 | 23280 | -36.1107
35 | 9603000023 | ITEM 34 | 4456000038 | 5)COST OF 11 KV CTPT SET 30/5 A | No. | 29183.42 | 32496.98 | 32153 | 23280 | -27.5962
36 | 9603000024 | ITEM 35 | 4456000040 | 6)COST OF 11 KV CTPT SET 40/5 A | No. | 28348.55 | 32496.98 | 32153 | 23280 | -27.5962
37 | 9603000025 | ITEM 36 | 4456000042 | 7)COST OF 11 KV CTPT SET 50/5 A | No. | 27785.94 | 32750 | 32153 | 23280 | -27.5962
38 | 9603000026 | ITEM 37 | 4456000043 | 8)COST OF 11 KV CTPT SET 75/5 A | No. | 24151.26 | 32297.88 | 32153 | 23280 | -27.5962
39 | 9603000027 | ITEM 38 | 4456000048 | 9)COST OF 11 KV CTPT SET 100/5A | No. | 23876.26 | 32097.88 | 32153 | 24367 | -24.2155
40 | 9603000064 | ITEM 39 | 4456000039 | 10)COST OF 11 KV CTPT SET 150/5 A | No. | 23876.26 | 32097.88 | 32153 | 24367 | -24.2155
41 | 9603000028 | ITEM 40 | 4456000045 | 11)COST OF 11 KV CTPT SET 200/5 A | No. | 23876.26 | 43497.36 | 39218 | 24367 | -37.8678
42 | 9603000056 | ITEM 41 | 4456000046 | 12)COST OF 11 KV CTPT SET 250/5 A | No. | 24151.26 | 43497.36 | 39218 | 24367 | -37.8678

## H2
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 2
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV DP STRUCTURE AT S/S END FOR O/H LINE AND U/G CABLE USING 11 MTR RSJ POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11MTR | NO. | 2 | 12986 | 25972
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS BRACING ANGLE SET (4 ANGLES/SET) | SET | 2 | 3336 | 6672
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV | No | 4 | 834 | 3336
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 65 | 1040
| 26 01 00 0049 | Side clamp | No | 16 | 65 | 1040
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | Thimbal for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 | [5 empty] | 51502.44
|  | COST OF MATERIALS |  |  |  | 51502.44
|  | ADD:3% CONTINGENCIES |  |  |  | 1545.0732
|  | ADD:2% STORAGE CHARGES |  |  |  | 1030.0488
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1030.0488
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 7725.366
|  | Total ….A |  |  |  | 62832.9768
11 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 246 | 492
DESTINATION
12 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
13 |  | LABOUR CHARGES FOR ERECTION OF D.P. |  |  |  |  | MM | 700 | 700 | 1400
|  | STRUCTURE ON RSJ POLE WITH | [5 empty] | L | B | H
|  | AB SWITCH/HG FUSE | SET | 1 | 2485 | 2485 |  | 0.7 | 0.7 | 1.4
[7 empty] | CMT | 0.686
14 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
15 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
16 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
17 |  | LABOUR CHARGES |  |  |  | 17410
18 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2611.5
19 |  | B |  |  |  | 20021.5
20 |  | Total ( A+B ) |  |  |  | 82854.4768
|  | Total Estimate |  |  | Say Rs. | 82854.4768

## H3
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 3
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 185 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1034 | 1034
|  | ADD:3% CONTINGENCIES |  |  |  | 31.02
|  | ADD:2% STORAGE CHARGES |  |  |  | 20.68
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 20.68
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 155.1
|  | Total ….A |  |  |  | 1261.48
B
2 | 9909000003 | Laying (including installation, testing and commissioning) of various size of Single circuit 11 KV XLPE insulated Aluminium armoured Cable in ground 1200 mm deep and 300 mm wide trench, providing sand cushioning below (75 mm thick layer of sand) and above (75 mm thick layer of sand) of the cable and covering it with RCC half round hume pipe (150 mm inner diameter with thickness of 30 mm and One meter in length) before refilling pre-bonding tap/warning tap should provide below 700 mm from the ground level and back filling the same to make ground level as per original. As per specification and drawing of UGVCL. ( RCC half round pipe should be provide throughout on cable without gap). Only Cable will be supplied by UGVCL. | Mtr. | 1 | 335 | 335 | new code generated | 335
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 50.25 |  | 50.25
4 |  | Total B |  |  |  | 385.25 |  | 385.25
5 |  | Total A + B |  |  |  | 1646.73 |  | 1646.73
|  | TOTAL |  |  | Say Rs. | 1646.73

## H4
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 4
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY DIGGING CABLE TRENCH
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 240 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1162 | 1162
|  | ADD:3% CONTINGENCIES |  |  |  | 34.86
|  | ADD:2% STORAGE CHARGES |  |  |  | 23.24
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 23.24
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 174.3
|  | Total ….A |  |  |  | 1417.64 |  | 1752
B
2 | 9909000003 | Laying (including installation, testing and commissioning) of various size of Single circuit 11 KV XLPE insulated Aluminium armoured Cable in ground 1200 mm deep and 300 mm wide trench, providing sand cushioning below (75 mm thick layer of sand) and above (75 mm thick layer of sand) of the cable and covering it with RCC half round hume pipe (150 mm inner diameter with thickness of 30 mm and One meter in length) before refilling pre-bonding tap/warning tap should provide below 700 mm from the ground level and back filling the same to make ground level as per original. As per specification and drawing of UGVCL. ( RCC half round pipe should be provide throughout on cable without gap). Only Cable will be supplied by UGVCL. | Mtr. | 1 | 335 | 335 | 375
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 50.25 | 56.25
4 |  | Total B |  |  |  | 385.25 | 431.25
5 |  | Total A + B |  |  |  | 1802.89 | 1848.89
|  | TOTAL |  |  | Say Rs. | 1802.89 | 1849

## H5.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 5
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV 185 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 185 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1034 | 1034
|  | ADD:3% CONTINGENCIES |  |  |  | 31.02
|  | ADD:2% STORAGE CHARGES |  |  |  | 20.68
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 20.68
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 155.1
|  | Total ….A |  |  |  | 1261.48
B
2 | 9909000003 | Providing and Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 110 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. | Mtr. | 1 | 1350 | 1350 | new code generated
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 202.5
4 |  | Total B |  |  |  | 1552.5
5 |  | Total A + B |  |  |  | 2813.98
|  | TOTAL |  |  | Say Rs. | 2813.98

## H6.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 6
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV 240 MM2 XLPE ALLUMINIUM, 3 CORE CABLE INCLUDING LAYING BY PUSH THROGH METHOD
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
A
1 | 0405000009 | 11KV 240 mm2 XLPE Alluminium, 3 Core Cable | Mtr. | 1 | 1162 | 1162
|  | ADD:3% CONTINGENCIES |  |  |  | 34.86
|  | ADD:2% STORAGE CHARGES |  |  |  | 23.24
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 23.24
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 174.3
|  | Total ….A |  |  |  | 1417.64
B
2 | 9909000003 | Providing & Laying of HDPE Pipe confirming to IS 4984:1955 (Amendment no. 2) having 160 mm Diameter and minimum 5 mm Thickness at a minimum Depth of 1200 mm below the road surface by Push through method, drilling the road with HDD machine/manually without breaking the road surface and laying of any size of HT XLPE insulated Aluminum armoured Cable through the duct as per the instruction of EIC and specifications including cost of HDPE Pipe. Only Cable will be supplied by UGVCL. | Mtr. | 1 | 1440 | 1440 | New code generaated | 1350
3 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 216
4 |  | Total B |  |  |  | 1656
5 |  | Total A + B |  |  |  | 3073.64
|  | TOTAL |  |  | Say Rs. | 3073.64

## H7.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 7
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV TAPPING FROM EXISTING POLE
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | STRAIGHT CROSS ARMS. (1.15 Mtr) | NO. | 2 | 341 | 682
| 36 11 00 0018 | M.S Angle Tapping-11KV FEBRI. 65x65x6x1150MM | NO. | 2 | 341 | 682
2 |  | BRACING FOR SIDE ARM | NO. | 2 | 224 | 448
| 36 11 00 0031 | Angle Bracing for D.P-65x65x6-750MM | NO. | 2 | 224 | 448
3 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 1 | 1057 | 1057
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 1 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
4 |  | 11KV PIN INSULATORS WITH SPINDLE | SET | 1 | 219 | 219
| 20 01 00 0006 | (a) 11 KV Pin Insulator | No | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | No | 1 | 0 | 0
219
5 |  | 11KV STRAIN INSULATORS WITH H/W | SET | 3 | 292 | 876
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
6 |  | M.S. BOLTS OF ASSORTED SIZES &
P.G. CLAMPS OR WITH PREFORMED
|  | FITTINGS. |  |  |  | 442
| 15 01 00 0024 | M.S. Bolts & Nuts - 65X16MM | KG | 1.6 | 70 | 112
| 2601 00 0027/28 | P.G. Clamp for Weasel/Rabbit | Nos | 3 | 110 | 330
442
7 |  | CLAMP FOR BRACING AND CROSS ARMS | PAIR | 1 | 130 | 130
| 26 01 00 0049 | Side clamp | Nos. | 2 | 65 | 130
8 |  | COST OF MATERIALS |  |  |  | 3854
9 |  | A |  |  |  | 3854
|  | ADD:3% CONTINGENCIES |  |  |  | 115.62
|  | ADD:2% STORAGE CHARGES |  |  |  | 77.08
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 77.08
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 578.1
|  | Total ….A |  |  |  | 4701.88
10 |  | LABOUR CHARGES FOR FIXING
|  | OF CROSS ARMS, BRACING ON LOCATION | NO. | 1 | 313 | 313
11 |  | ERECTION OF STAY SETS. | NO. | 1 | 364 | 364
12 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.15 | 5900 | 885
13 |  | LABOUR CHARGES |  |  |  | 1562
14 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 234.3
15 |  | B |  |  |  | 1796.3
16 |  | Sub Total(A+B) |  |  |  | 6498.18
|  | Total Estimate |  |  | Say Rs. | 6498.18
Note on F24: R C DESAI(SIR): BASE OLD RATE AS CURRENT RATE IS LOW

## H8.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 8
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D. P. STRUCTURE WITH A. B. SWITCH USING 8 MTR PSC POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2017 | 4034 |  | Material Code | Material Name | Uom | Qty | Unit Value | Flag | Margin Value | Company % | Consumer %
[7 empty] | 1270 | 3611000016 | MS ANGLE TOP FAB 65X65X6MM 11KV 2750MM | NO | 2 | 635 | PERCENT | 0 | 0 | 100
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668 | 1270 | 3611000038 | MS ANGLE 11KV HG FUSE FABRICATED65X65X6X2750MM | NO | 2 | 635 | PERCENT | 0 | 0 | 100
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668 | 549.648 | 1501000024 | M S BOLTS AND NUTS 65 MM X 16 MM_( 2.5 X 5/8 INCH) | KG | 7.2 | 76.34 | PERCENT | 0 | 0 | 100
[7 empty] | 190.0866 | 1501000031 | M S BOLTS AND NUTS 180 MM X 16 MM_( 7 X 5/8 INCH ) | KG | 2.49 | 76.34 | PERCENT | 0 | 0 | 100
3 |  | CROSS ARM FOR MOUNTING A.B SWITCH. | NO. | 2 | 834 | 1668 | 28 | 1905000006 | HT ADHESIVE TAPE ROLLS | NO | 20 | 1.4 | PERCENT | 0 | 0 | 100
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668 | 480 | 2601000069 | STAY CLAMP FOR PSC POLES | PR | 4 | 120 | PERCENT | 0 | 0 | 100
[7 empty] | 1863.3 | 2006000001 | 11 KV DISC INSULATOR PLAIN 7000 KG | NO | 6 | 310.55 | PERCENT | 0 | 0 | 100
[7 empty] | 76 | 2003000001 | GUY INSULATOR H .T PORCELAIN | NO | 4 | 19 | PERCENT | 0 | 0 | 100
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658 | 899.82 | 2010000077 | 11 KV DISC HARDWARE | SET | 6 | 149.97 | PERCENT | 0 | 0 | 100
[7 empty] | 720 | 2601000027 | PG CLAMPS FOR WEASEL | NO | 9 | 80 | PERCENT | 0 | 0 | 100
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS FOR | NO. | 4 | 65 | 260 | 204 | 2601000049 | C CLAMP FOR PSC POLES | NO | 4 | 51 | PERCENT | 0 | 0 | 100
|  | A B Switch |  |  |  |  | 140 | 2801000015 | PVC RIGID PIPE 20M M | MTR | 2 | 70 | PERCENT | 0 | 0 | 100
| 26 01 00 0049 | Side clamp | No | 4 | 65 | 260 | 40 | 101000003 | ALL ALUM BINDING WIRE 8 SWG 4 MM | KG | 0.5 | 80 | PERCENT | 0 | 0 | 100
[7 empty] | 351.6 | 103000002 | G I WIRE 8 SWG 4MM | KG | 6 | 58.6 | PERCENT | 0 | 0 | 100
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228 | 1140 | 103000012 | G I STAY WIRE 7/10 SWG 7/3.15 MM | KG | 20 | 57 | PERCENT | 0 | 0 | 100
|  | Material required for1 No. Guy set |  |  |  |  | 5071 | 613000003 | 11 KV G.O SWITCH W/O EARTH BLADE 400 AMP | SET | 1 | 5071 | PERCENT | 0 | 0 | 100
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258 | 3460 | 2611000003 | PSC POLES 200 KG 8 METER READY MADE | No | 2 | 1730 | PERCENT | 0 | 0 | 100
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145 | 1224 | 2614000002 | ANCHOR RODS | NO | 4 | 306 | PERCENT | 0 | 0 | 100
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74 | 440 | 2614000009 | TURN BUCKLE MS 16MM | NO | 4 | 110 | PERCENT | 0 | 0 | 100
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365 | 188 | 2614000012 | EYE BOLT WITH NUT | NO | 4 | 47 | PERCENT | 0 | 0 | 100
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30 | 19605.4546
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  |  | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 23780.44
11 |  | A |  |  |  | 23780.44
|  | ADD:3% CONTINGENCIES |  |  |  | 713.4132
|  | ADD:2% STORAGE CHARGES |  |  |  | 475.6088
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 475.6088
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 3567.066
|  | Total ….A |  |  |  | 29012.1368
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 246 | 492
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON PSC POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 2067 | 2067
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
18 |  | LABOUR CHARGES |  |  |  | 8623
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1293.45
20
21 |  | B |  |  |  | 9916.45
22 |  | Sub Total(A+B) |  |  |  | 38928.5868
|  | Total Estimate |  |  | Say Rs. | 38928.5868

## H9.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 9
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D. P. STRUCTURE WITH H.G. FUSE USING 8 MTR PSC POLES (WITHOUT AB SWITCH)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8M/ 200 KG | NO. | 2 | 2017 | 4034
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING HG FUSE | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
5 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 65 | 130
FOR HG FUSE.
| 26 01 00 0049 | Side clamp | No | 2 | 65 | 130
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 128 | 128
292
9 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
10 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1518.44
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 70 | 364
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601000027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1518.44
11 |  | COST OF MATERIALS |  |  |  | 18060.62
12 |  | A |  |  |  | 18060.62
|  | ADD:3% CONTINGENCIES |  |  |  | 541.8186
|  | ADD:2% STORAGE CHARGES |  |  |  | 361.2124
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 361.2124
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 2709.093
|  | Total ….A |  |  |  | 22033.9564
13 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 246 | 492
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE,HG FUSE | SET | 1 | 2067 | 2067
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
15 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
16 |  | LABOUR CHARGES |  |  |  | 8623
17 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1293.45
18 |  | B |  |  |  | 9916.45
19 |  | Sub Total(A+B) |  |  |  | 31950.4064
|  | Total Estimate |  |  | Say Rs. | 31950.4064

## H10.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 10
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D. P. STRUCTURE A. B. SWITCH USING 9 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 2 | 10478 | 20956
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING HG FUSE/A.B SWITCH. | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 65 | 1040
| 26 01 00 0049 | Side clamp | No | 16 | 65 | 1040
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  |  | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/28 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 41482.44
11 |  | A |  |  |  | 41482.44
|  | ADD:3% CONTINGENCIES |  |  |  | 1244.4732
|  | ADD:2% STORAGE CHARGES |  |  |  | 829.6488
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 829.6488
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 6222.366
|  | Total ….A |  |  |  | 50608.5768
12 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 246 | 492
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON RSJ POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 2485 | 2485
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
18 |  | LABOUR CHARGES |  |  |  | 17065
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2559.75
20
21 |  | B |  |  |  | 19624.75
22 |  | Sub Total(A+B) |  |  |  | 70233.3268
|  | Total Estimate |  |  | Say Rs. | 70233.3268

## H11.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 11
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D. P. STRUCTURE WITH H.G. FUSE USING 9 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110*9MTR | NO. | 2 | 10478 | 20956
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING HG FUSE | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 65 | 130
FOR HG FUSE.
| 26 01 00 0049 | Side clamp | No | 2 | 65 | 130
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 128 | 128
292
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1518.44
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 70 | 364
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1518.44
10 |  | COST OF MATERIALS |  |  |  | 34982.62
11 |  | A |  |  |  | 34982.62
|  | ADD:3% CONTINGENCIES |  |  |  | 1049.4786
|  | ADD:2% STORAGE CHARGES |  |  |  | 699.6524
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 699.6524
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 5247.393
|  | Total ….A |  |  |  | 42678.7964
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 246 | 492
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
13 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE,HG FUSE | SET | 1 | 2485 | 2485
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
14 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
15 |  | LABOUR CHARGES |  |  |  | 9041
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1356.15
17 |  | B |  |  |  | 10397.15
18 |  | Sub Total(A+B) |  |  |  | 53075.9464
|  | Total Estimate |  |  | Say Rs. | 53075.9464

## H12.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 11
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D. P. STRUCTURE WITH H.G. FUSE USING 9 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | RSJ POLE 116*110* 11MTR | NO. | 2 | 12986 | 25972
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING HG FUSE/A.B SWITCH. | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 | 06 13 00 0003 | 11 KV A.B. SWITCH 400 AMP. | SET | 1 | 7658 | 7658
5 |  | SIDE CLAMP FOR MOUNTING AB SWITCH | NO. | 16 | 65 | 1040
| 26 01 00 0049 | Side clamp | No | 16 | 65 | 1040
6 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
|  | Material required for 1 No. earthing |  |  |  | 1057
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | Set | 1 | 128 | 128
292
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1988.44
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 7.2 | 70 | 504
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/028 | (c) P.G.Clamp for Weasel or Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1988.44
10 |  | COST OF MATERIALS |  |  |  | 46498.44
11 |  | A |  |  |  | 46498.44
|  | ADD:3% CONTINGENCIES |  |  |  | 1394.9532
|  | ADD:2% STORAGE CHARGES |  |  |  | 929.9688
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 929.9688
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 6974.766
|  | Total ….A |  |  |  | 56728.0968
12 |  | (A) CARTING OF RSJ POLE AT | NO. | 2 | 246 | 492
DESTINATION
13 |  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
14 |  | LABOUR CHARGES FOR ERECTION OF D.P.
STRUCTURE ON RSJ POLE WITH
|  | AB SWITCH/HG FUSE | SET | 1 | 2485 | 2485
15 |  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
16 |  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
17 |  | CONCRETING OF POLE & GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
18 |  | LABOUR CHARGES |  |  |  | 17410
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 2611.5
20 |  | B |  |  |  | 20021.5
21 |  | Sub Total(A+B) |  |  |  | 76749.5968
|  | Total Estimate |  |  | Say Rs. | 76749.5968

## H13.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 13
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D. P. STRUCTURE H.G.FUSE USING 11 MTR RSJ POLES.
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000013 | RSJ POLE 116*110* 11MTR | NO. | 2 | 12986 | 25972
2 |  | TOP CROSSARM FOR TERMINATING LINE | NO. | 2 | 834 | 1668
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750MM FOR TOP FABRI. | No | 2 | 834 | 1668
3 |  | CROSS ARM FOR MOUNTING HG FUSE | NO. | 2 | 834 | 1668
| 36 11 00 0038 | M.S.Angle 11 KV HG Fuse - Fabri 65x65x6mm- 2750mm | No | 2 | 834 | 1668
4 |  | SIDE CLAMP FOR FIXING CROSS ARMS | NO. | 2 | 65 | 130
FOR HG FUSE.
| 26 01 00 0049 | Side clamp | No | 2 | 65 | 130
5 |  | GUY SET WITH PREFORMED FITTINGS | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | ( c ) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 |  | EARTHING OF STRUCTURE.-COIL TYPE | NO. | 2 | 262 | 524
Material required for 1 No. earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
7 |  | 11 KV STRAIN INSULATORS WITH | SET | 6 | 292 | 1752
H/W OF PREFORMED FITTING.
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO | 1 | 164 | 164
| 20 10 00 0007 | (b) 11KV Disc. Hardware | SET | 1 | 128 | 128
292
8 | 13 05 00 0001 | 11 KV H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
9 |  | SUNDRIES MATERIALS SUCH AS BOLT
NUTS/PG CLAMPS/BINDING TAPE &
|  | BINDING WIRE ETC.OR WITH PER. FITTING |  |  |  | 1518.44
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 5.2 | 70 | 364
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 2.492 | 70 | 174.44
| 2601 00 0027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
1518.44
10 |  | COST OF MATERIALS |  |  |  | 39998.62
11 |  | A |  |  |  | 39998.62
|  | ADD:3% CONTINGENCIES |  |  |  | 1199.9586
|  | ADD:2% STORAGE CHARGES |  |  |  | 799.9724
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 799.9724
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 5999.793
|  | Total ….A |  |  |  | 48798.3164
12 |  | (A) CARTING OF PSC POLE AT | NO. | 2 | 246 | 492
DESTINATION
|  | (B) CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 230
13 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON RSJ POLE,HG FUSE | SET | 1 | 2485 | 2485
|  | II. INSTALLATION OF EARTHING COIL | NO. | 2 | 419 | 838
TYPE COMP. WITH SALT & COAL
|  | III. PROVINDING GUY SET WITH ALL | NO. | 4 | 364 | 1456
ACCESSORIES & FITTINGS.
14 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
15 |  | LABOUR CHARGES |  |  |  | 9041
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 1356.15
17 |  | B |  |  |  | 10397.15
18 |  | Sub Total(A+B) |  |  |  | 59195.4664
|  | Total Estimate |  |  | Say Rs. | 59195.4664

## H14.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 14
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 55MM2 AAA CONDUCTOR USING 8 MTR/ 200 KG PSC POLES. WPZ - 100 KG/M2(SPAN 50 MTRS.)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 20 | 2017 | 40340
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 555 | 11100
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 2 | 1057 | 2114
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
[6 empty] | 1057 | 0
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
|  | Material required for 1 No earthing |  |  |  |  | 0
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 219 | 13140
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL. |  | 12 | 292 | 3504
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 3218.2
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 11.6 | 70 | 812
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 15.66 | 70 | 1096.2
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 9 | 110 | 990
| 19 05 00 0006 | (d) Binding tape | Mtr | 20 | 13 | 260
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.5 | 120 | 60
3218.2
14 |  | COST OF MATERIALS |  |  |  | 183056.12
15 |  | A |  |  |  | 183056.12
|  | ADD:3% CONTINGENCIES |  |  |  | 5491.6836
|  | ADD:2% STORAGE CHARGES |  |  |  | 3661.1224
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 3661.1224
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 27458.418
|  | Total ….A |  |  |  | 223328.4664
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF PSC POLES AT DESTI. | NO. | 20 | 246 | 4920
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 757 | 15140
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 2 | 364 | 728
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.3 | 5900 | 1770
24 |  | LABOUR CHARGES |  |  |  | 36032
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 5404.8
26 |  | B |  |  |  | 41436.8
27 |  | Sub Total(A+B) |  |  |  | 264765.2664
|  | Total Estimate |  |  | Say Rs. | 264765.2664

## H15.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 15
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-33 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 30 | 12986 | 389580
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 555 | 16650
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 219 | 19710
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
11 |  | 11KV STRAIN INSULATOR COMPL. |  | 24 | 292 | 7008
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
4998
14 |  | COST OF MATERIALS |  |  |  | 560227.92
15 |  | A |  |  |  | 560227.92
|  | ADD:3% CONTINGENCIES |  |  |  | 16806.8376
|  | ADD:2% STORAGE CHARGES |  |  |  | 11204.5584
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 11204.5584
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 84034.188
|  | Total ….A |  |  |  | 683478.0624
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 246 | 7380
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1268 | 38040
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5900 | 125670
24 |  | LABOUR CHARGES |  |  |  | 190938
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 28640.7
26 |  | B |  |  |  | 219578.7
27 |  | Sub Total(A+B) |  |  |  | 903056.7624
|  | Total Estimate |  |  | Say Rs. | 903056.7624

## H16.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 16
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE-11 MTR (SPAN-50 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 20 | 12986 | 259720
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 555 | 11100
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 219 | 13140
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 292 | 7008
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
4998
14 |  | COST OF MATERIALS |  |  |  | 411947.92
15 |  | A |  |  |  | 411947.92
|  | ADD:3% CONTINGENCIES |  |  |  | 12358.4376
|  | ADD:2% STORAGE CHARGES |  |  |  | 8238.9584
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 8238.9584
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 61792.188
|  | Total ….A |  |  |  | 502576.4624
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 246 | 4920
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1268 | 25360
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF RSJ & GUY WITH MATERIAL(1:2:4) | CMT | 14.5 | 5900 | 85550
24 |  | LABOUR CHARGES |  |  |  | 131488
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 19723.2
26 |  | B |  |  |  | 151211.2
27 |  | Sub Total(A+B) |  |  |  | 653787.6624
|  | Total Estimate |  |  | Say Rs. | 653787.6624

## H17.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 17
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON RSJ/TUBULAR POLE- 9 MTR (SPAN-50 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*9 MTR | NO. | 20 | 10478 | 209560
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 20 | 555 | 11100
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 60 | 219 | 13140
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 292 | 7008
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
4998
14 |  | COST OF MATERIALS |  |  |  | 361787.92
15 |  | A |  |  |  | 361787.92
|  | ADD:3% CONTINGENCIES |  |  |  | 10853.6376
|  | ADD:2% STORAGE CHARGES |  |  |  | 7235.7584
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 7235.7584
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 54268.188
|  | Total ….A |  |  |  | 441381.2624
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 246 | 4920
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1268 | 25360
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119 | GUY .15
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 14.5 | 5900 | 85550 | 14.5
24 |  | LABOUR CHARGES |  |  |  | 131488
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 19723.2
26 |  | B |  |  |  | 151211.2
27 |  | Sub Total(A+B) |  |  |  | 592592.4624
|  | Total Estimate |  |  | Say Rs. | 592592.4624

## H18.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 18
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 55 MM2 AAAC CONDUCTOR WITH WIND PRESSURE 100 KG/M2 ON PSC POLE(SPAN-33 MTR)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 M/200KG. | NO. | 30 | 2017 | 60510
2 | 26 09 00 0034 | 11KV V CROSS ARM. | NO. | 30 | 555 | 16650
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 11KV PIN INSULATOR COMPL. | NO. | 90 | 219 | 19710
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)11 KV Pin Insulator | NO. | 1 | 219 | 219
| 20 10 00 0010 | (b) 11 KV GI Pin | NO. | 1 | 0 | 0
219
11 |  | 11KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 292 | 7008
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR 55MM2 SIZE | KM. | 3.09 | 31288 | 96679.92
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 6131.3
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 19 | 70 | 1330
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 25.99 | 70 | 1819.3
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
6131.3
14 |  | COST OF MATERIALS |  |  |  | 230177.22
15 |  | A |  |  |  | 230177.22
|  | ADD:3% CONTINGENCIES |  |  |  | 6905.3166
|  | ADD:2% STORAGE CHARGES |  |  |  | 4603.5444
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 4603.5444
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 34526.583
|  | Total ….A |  |  |  | 280816.2084
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF PSC POLES AT DESTI. | NO. | 30 | 246 | 7380
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 757 | 22710
OF PSC POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 1373 | 4119
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 4 | 364 | 1456
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 0.6 | 5900 | 3540
24 |  | LABOUR CHARGES |  |  |  | 52750
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 7912.5
30
26 |  | B |  |  |  | 60662.5
27 |  | Sub Total(A+B) |  |  |  | 341478.7084
|  | Total Estimate |  |  | Say Rs. | 341478.7084

## H19.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 19
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (33 MTR. SPAN)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 30 | 12986 | 389580
2 | 26 09 00 0034 | 22KV V CROSS ARM. | NO. | 30 | 720 | 21600
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 30 | 65 | 1950
| 26 01 00 0049 | Side clamp | No | 30 | 65 | 1950
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 30 | 123 | 3690
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 30 | 262 | 7860
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 30 | 120 | 3600
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 30 | 120 | 3600
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 30 | 60 | 1800
10 |  | 22KV PIN INSULATOR COMPL. | NO. | 90 | 0 | 0
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 1 | 0 | 0
| 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 1 | 0 | 0
0
11 |  | 22KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
456
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 4998
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 28.8 | 70 | 2016
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 24 | 110 | 2640
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
4998
14 |  | COST OF MATERIALS |  |  |  | 632061.42
15 |  | A |  |  |  | 632061.42
|  | ADD:3% CONTINGENCIES |  |  |  | 18961.8426
|  | ADD:2% STORAGE CHARGES |  |  |  | 12641.2284
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 12641.2284
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 94809.213
|  | Total ….A |  |  |  | 771114.9324
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 30 | 246 | 7380
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 30 | 1268 | 38040
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 3162 | 9486
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 30 | 419 | 12570
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 21.3 | 5900 | 125670
24 |  | LABOUR CHARGES |  |  |  | 196305
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 29445.75
26 |  | B |  |  |  | 225750.75
27 |  | Sub Total(A+B) |  |  |  | 996865.6824
|  | Total Estimate |  |  | Say Rs. | 996865.6824

## H20.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 20
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV LINE WITH 100MM2 AAA "DOG" CONDUCTOR USING 116MM X 100MM X 11MTR LONG RSJ POLE (50 MTR SPAN)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*110*11 MTR | NO. | 20 | 12986 | 259720
2 | 26 09 00 0034 | 22KV V CROSS ARM. | NO. | 20 | 720 | 14400
3 |  | BACK CLAMP FOR FIXING CROSS ARMS. | NO. | 20 | 65 | 1300
| 26 01 00 0049 | Side clamp | No | 20 | 65 | 1300
4 | 26 01 00 0084 | TOP INSULATOR FITTING. | NO. | 20 | 123 | 2460
5 |  | TWO WAY STRAIN CLAMP. | NO. | 2 | 180 | 360
| 26 01 00 0071 | Guy clamp for two way strain clamp | No | 2 | 180 | 360
6 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
7 |  | EARTHING OF POLES (COIL TYPE) | NO. | 20 | 262 | 5240
Material required for 1 No earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 3 Kg | KG | 3 | 73 | 219
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO | 1 | 43 | 43
262
8 |  | ANTICLIMBING DEVICES. | NO. | 20 | 120 | 2400
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 20 | 120 | 2400
9 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 20 | 60 | 1200
10 |  | 22KV PIN INSULATOR COMPL. | NO. | 60 | 0 | 0
WITH H/W & PREFORM FITTING.
| 20 01 00 0006 | (a)22 KV Pin Insulator | NO. | 1 | 0 | 0
| 20 10 00 0010 | (b) 22 KV GI Pin | NO. | 1 | 0 | 0
0
11 |  | 22KV STRAIN INSULATOR COMPL.
|  | WITH H/W & PREFORM FITTING. | NO. | 24 | 456 | 10944
| 20 06 00 0001 | (a) 11KV Disc. Insulator | NO. | 2 | 164 | 328
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
456
12 | 01 02 00 0033 | AL.ALLOY CONDUCTOR DOG | KM. | 3.09 | 58038 | 179337.42
13 |  | SUNDRY MATERIAL SUCH AS PG |  |  |  | 342
CLAMP;BINDING WIRE,TAPS,BOLT,
NUTS WITH PREFORM FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 0 | 70 | 0
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 0 | 70 | 0
| 26 0100 0028 | (c) P.G. Clamp for Rabbit | No | 0 | 110 | 0
| 01 01 00 0003 | (d) Alu. Binding wire | KG | 0.9 | 120 | 108
| 19 05 00 0006 | (e) HT Tape | Mtr | 18 | 13 | 234
342
14 |  | COST OF MATERIALS |  |  |  | 484045.42
15 |  | A |  |  |  | 484045.42
|  | ADD:3% CONTINGENCIES |  |  |  | 14521.3626
|  | ADD:2% STORAGE CHARGES |  |  |  | 9680.9084
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 9680.9084
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 72606.813
|  | Total ….A |  |  |  | 590535.4124
16 |  | SURVEY,TREE CUTTING, COMPENSATION. |  |  | -L.S- | 400
17 |  | CARTING OF RSJ POLES AT DESTI. | NO. | 20 | 246 | 4920
18 |  | CARTING OF LINE MATERIAL TO WORK SITE. |  |  | -L.S- | 575
19 |  | LABOUR CHARGES FOR ERECTION | NO. | 20 | 1268 | 25360
OF RSJ POLE INCLUDING DIGGING.
OF PITS,FIXING OF POLES FIXTURE,
INSULATOR & PAINTING STEEL POLE
20 |  | STRINGING OF CONDUCTOR. | NO. | 3 | 3162 | 9486
21 |  | LABOUR CHARGES FOR FIXING GUYS. | NO. | 6 | 364 | 2184
22 |  | LABOUR CHARGES FOR PROVIDING | NO. | 20 | 419 | 8380
EARTHING WITH SALT & COAL.
23 |  | CONCRETING OF POLE& GUY WITH MATERIAL(1:2:4) | CMT | 14.5 | 5900 | 85550
24 |  | LABOUR CHARGES |  |  |  | 136855
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 20528.25
26 |  | B |  |  |  | 157383.25
27 |  | Sub Total(A+B) |  |  |  | 747918.6624
|  | Total Estimate |  |  | Say Rs. | 747918.6624

## H21.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 21
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV RAILWAY CROSSING BY 185 MM2 U/G XLPE CABLE. ( DOUBLE CKT 115 MTR LENGTH)
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 36 04 00 0001 | RSJ 116*100 MM 9 MTR. | NO. | 4 | 10478 | 41912
2 | 26 09 00 0034 | V CROSS ARMS 11KV | NO. | 4 | 555 | 2220
3 |  | STRAIN INSULATOR 11 KV WITH H/W | SET | 6 | 292 | 1752
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | No | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | Set | 1 | 128 | 128
292
4 | 04 05 00 0009 | 11 KVXLPE CABLE 3 CORE 185 mm2 SIZE.(Double CKT) | MTR | 230 | 1034 | 237820
5 |  | ANTI-CLIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | No | 2 | 120 | 240
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | GUY SET WITH PREFORM FITTING. | NO. | 6 | 1057 | 6342
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
|  | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
8 |  | SUNDRY MATERIAL SUCH AS |  |  |  | 1498
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 6.4 | 70 | 448
| 19 05 00 0006 | (b) HT Binding Tape | Mtr | 30 | 13 | 390
| 2601 00 0027/28 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
1498
9 |  | COST OF MATERIALS |  |  |  | 291904
10 |  | A |  |  |  | 291904
|  | ADD:3% CONTINGENCIES |  |  |  | 8757.12
|  | ADD:2% STORAGE CHARGES |  |  |  | 5838.08
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 5838.08
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 43785.6
|  | Total ….A |  |  |  | 356122.88
11 |  | LABOUR CHARGES FOR COMPLETE |  |  | ----LS---- | 350000
WORK OF CROSSING
(INCLUDING LAYING, JOINTING, INSERTATIOIN OF 150MM DIA C. I. PIPE UNDER RAILWAY TRACK USING HORIZONTAL AUGER GUIDED BORING BY PUSH THROUGH METHOD; INSERTATION OF C. I. PIPE IN SIDE RAILWAY BOUNDRY BY CUT AND FILL METHOD; PROVIDING AND SUPPLY OF 150MM DIA C. I. PIPE; LAYING OF 11KV XLPE CABLE IN SIDE C. I. PIPE; PROVIDING SUPPLY AND FIXING 185MM2 CABLE BOX, TERMINATION KIT; PROVIDING PAINTING, FABRICATION AND FIXING OF CABLE MARKER; PROVIDING AND FIXING OF G. I, PIPE ON ERECTED STRUCTURE FOR MECHANICAL PROTECTION OF XLPE CABLE & PROVIDING EARTHING AS PER RAILWAY AUTHORITY ETC.) THE FOLLOWING ITEMS ARE COVERED IN THE SCOPE OF SUPPLIER/CONTRACTOR. LENGTH OF CI PIPE, EARTHING, ITS INSTALLATION EVERYTHING BETWEEN TWO END TERMINATION ACROSS THE RAILWAY TRACK SHALL BE ACCORDING TO DRAWING APPROVED BY CONCERN RAILWAY AUTHORITY. CABLE WILL BE CARTED FROM STORE TO SITE BY CONTRACTOR. ONLY CABLE WILL BE PROVIDED BY UGVCL.
12 |  | CARTING OF RSJ POLE AT DEST. | NO. | 2 | 246 | 492
13 |  | CARTING OF LINE MATERIAL AT |  |  | ----LS---- | 575
WORK SITE
14 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 2.26 | 5900 | 13334
15 |  | LABOUR CHARGES |  |  |  | 364401
16 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 54660.15
17 |  | B |  |  |  | 419061.15
18 |  | Sub Total(A+B) |  |  |  | 775184.03
|  | Total Estimate |  |  | Say Rs. | 775184.03

## H22.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 22
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
GUARDING FOR H.T./ L.T.LINES AND P&T LINES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 |  | GUARDING ANGLE CROSS ARM | NO. | 2 | 607 | 1214
| 26 09 00 0029/ 31 | M.S.Angle 65x65x6mm - 2 Mtr for Guarding Angle cross arm/Guarding channel | No | 2 | 607 | 1214
2 |  | BACK CLAMP | NO. | 2 | 65 | 130
| 26 01 00 0049 | Side clamp | No | 2 | 65 | 130
3 | 01 03 00 0003 | G.I. WIRE 10 SWG | KG. | 2 | 70 | 140
4 | 01 03 00 0002 | G.I. WIRE NO. 8 | KG. | 14 | 73 | 1022
5 |  | MISC. ITEMS i.e.BOLTS ,NUTS |  |  |  | 376
WASHER,BINDING WIRES.
| 26 14 00 0012 | Eye-bolt | No | 4 | 74 | 296
| 15 01 00 0024 | Bolts & Nuts - 65x16mm | KG | 0.8 | 70 | 56
| 01 01 00 0003 | Alu.Binding wire | KG | 0.2 | 120 | 24
376
6 |  | COST OF MATERIALS |  |  |  | 2882
7 |  | A |  |  |  | 2882
|  | ADD:3% CONTINGENCIES |  |  |  | 86.46
|  | ADD:2% STORAGE CHARGES |  |  |  | 57.64
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 57.64
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 432.3
|  | Total ….A |  |  |  | 3516.04
8 |  | LABOUR CHARGES FOR FIXING | NO. | 2 | 313 | 626
OF CROSS ARMS ON LOCATION.
9 |  | PROVIDE GUARDING. | MTR | 60 | 58 | 3480
COMPLETE WITH PAINTING.
10 |  | LABOUR CHARGES |  |  |  | 4106
11 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 615.9
12
13 |  | B |  |  |  | 4721.9
14 |  | Sub Total(A+B) |  |  |  | 8237.94
|  | Total Estimate |  |  | Say Rs. | 8237.94

## H23.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 23
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 8 MTR PSC POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 8 Meter 200 KG | NO. | 2 | 2017 | 4034
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | ---LS--- |  |  | 11624
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 1287 | 2574
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
11624
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 438 | 1314
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | HT SMC Box | NO. | 1 | 2714 | 2714
10 |  | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 5 | 175 | 875
| 04 01 00 0004 | Doble Compressed 25 mm2 Cable Gland | No. | 0 | 135 | 0
|  | Test Terminal Box | No. | 1 | 875 | 875
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 0 | 82.83 | 0
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 0 | 82.83 | 0
12 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 1012 | 1012
| 1607000009 | (i) 3-ph MMB | NO | 1 | 882 | 882
| 2601000061 | (ii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
1012
13 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2496.78
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/ 28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 14 | 42
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 3.54 | 7.08
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 3.2 | 19.2
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 2.7 | 5.4
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2496.78
14 |  | COST OF MATERIALS |  |  |  | 32997.96
15 |  | A |  |  |  | 32997.96
|  | ADD:3% CONTINGENCIES |  |  |  | 989.9388
|  | ADD:2% STORAGE CHARGES |  |  |  | 659.9592
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 659.9592
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 4949.694
|  | Total ….A |  |  |  | 40257.5112
16 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
17 |  | DIST.BOX ETC. | NO. | 1 | 5900 | 5900
18 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
19 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
20 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
21 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
22 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
23 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
24 |  | LABOUR CHARGES… |  |  |  | 21794
25 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3269.1
26 |  | B |  |  |  | 25063.1
27 |  | Sub Total(A+B) |  |  |  | 65320.6112
|  | Total Estimate |  |  | Say Rs. | 65320.6112

## H24.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 24
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 11 MTR RSJ POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 11 Meter | NO. | 2 | 12986 | 25972
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | NO. | 1 | 10718 | 10718
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 834 | 1668
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
10718
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 438 | 1314
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | HT SMC Box | NO. | 1 | 2714 | 2714 | check
10 |  | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 5 | 175 | 875
| 04 01 00 0004 | Doble Compressed 25 mm2 Cable Gland | No. | 2 | 135 | 270
|  | Test Terminal Box | No. | 1 | 875 | 875
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 0 | 82.83 | 0
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 0 | 82.83 | 0
12 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 1 | 1012 | 1012
| 1607000034 | (i) 3-ph SMC Box | NO | 1 | 882 | 882
| 2601000061 | (ii) SIDE CLAMPS (50x6mm) | NO | 2 | 65 | 130
1012
13 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2496.78
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 26 01 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 14 | 42
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 3.54 | 7.08
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 3.2 | 19.2
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 2.7 | 5.4
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2496.78
14 |  | COST OF MATERIALS |  |  |  | 54299.96
15 |  | A |  |  |  | 54299.96
|  | ADD:3% CONTINGENCIES |  |  |  | 1628.9988
|  | ADD:2% STORAGE CHARGES |  |  |  | 1085.9992
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1085.9992
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 8144.994
|  | Total ….A |  |  |  | 66245.9512
16 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899
17 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
18 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
19 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
20 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
22 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
23 |  | LABOUR CHARGES… |  |  |  | 22793
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3418.95
25 |  | B |  |  |  | 26211.95
26 |  | Sub Total(A+B) |  |  |  | 92457.9012
|  | Total Estimate |  |  | Say Rs. | 92457.9012

## H25.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 25
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
11KV D.P. STRUCTURE AT CONSUMER END WITH H.G. FUSES AND LA FOR MOUNTING CTPT SET USING 9 MTR RSJ POLES
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 9 Meter | NO. | 2 | 10478 | 20956
2 |  | STRUCTURE STEEL FOR TERMINATING
|  | LINES MOUNTING OF TRANS.FIXING | NO. | 1 | 10718 | 10718
OF FUSES 11KV.
| 36 12 00 0005 | (a) M.S.Channel Bottom Fab. For Trns. DP - 100x50x6mm - 3340mm | NO | 4 | 1530 | 6120
| 36 11 00 0038 | (b) M.S.Angle 11 KV HG Fuse- Fab. 65x65x6mm - 2750mm | NO | 2 | 834 | 1668
| 36 12 00 0026 | (c) M.S.Angle Fab. 65x65x6mm -2745mm for belting | NO | 2 | 834 | 1668
| 36 12 00 0023 | (d) M.S. Angle Fab. 65x65x6mm -810mm for side arms for HG fuse | NO | 4 | 241 | 964
| 26 09 00 0008 | (e) M.S.Angle 65x65x6mm - 1 Mtr for Distribution box | NO | 1 | 298 | 298
10718
3 | 13 05 00 0001 | 11 KV.H.G. FUSES. | NO. | 3 | 846.06 | 2538.18
4 | 22 01 00 0004 | 11KV DIST.TYPE LIGHTENING ARRESTOR | NO. | 3 | 309 | 927
5 |  | GUY SET WITH PREFORMED FITTING. | NO. | 4 | 1057 | 4228
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 2 | 60 | 120
7 |  | EARTHING FOR POLE NEUTRAL & LIGHTING | NO. | 3 | 438 | 1314
ARRESTOR (PIPE )
Material required for 1 No Plate Type earthing
| 09 01 00 0007 | (a) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 28 01 00 0015 | (b) Rigid PVC Pipe 20mm dia ( 1.5 Mtr) - 1 No | NO. | 1 | 43 | 43
| 01 03 00 0002 | (c) G.I. wire No.8 - .848 Kg | KG | 1 | 73 | 73
| 09 01 00 0028 | (d) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | ANTI CLAIMBING DEVICES. | NO. | 2 | 120 | 240
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 2 | 120 | 240
9 | 21 04 00 0006 | HT SMC Box | NO. | 1 | 2714 | 2714
10 |  | PVC INSULATED & SHEATHED 2.5 MM2 10 Core Armoured Copper Control Cable | MTR | 5 | 175 | 875
| 04 01 00 0004 | Double Compressed 25 mm2 Cable Gland | No. | 2 | 135 | 270
|  | Test Terminal Box | No. | 0 | 875 | 0
11 |  | -DO- BUT 25 MM2 OUT GOING SIDE. | MTR | 0 | 82.83 | 0
| 04 01 00 0001 | 3.5Cx 25MM2 LT PVC Cable | MTR | 0 | 82.83 | 0
12 |  | Static Meter for energy audit of T/C along with MMB/CTS Cable | SET | 0 | 0 | 0
| 1607000034 | (i) 3-ph SMC Box | NO | 0 | 882 | 0
| 2601000061 | (ii) SIDE CLAMPS (50x6mm) | NO | 0 | 65 | 0
0
13 |  | SUNDRY MATERIALS SUCH AS PG
|  | CLAMPS, BOLTS & NUTS ETC. |  |  |  | 2496.78
| 15 01 00 0024 | (a) M.S.Bolts & Nuts 65x16mm | KG | 4 | 70 | 280
| 15 01 00 0031 | (b) M.S.Bolts & Nuts 180x16mm | KG | 3.56 | 70 | 249.2
| 15 01 00 0038 | (c) M.S.Bolts & Nuts 300x16mm | KG | 3.09 | 70 | 216.3
| 2601 00 0027/28 | (d) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 13 02 00 0005 | (e) Fuse element - 5 Amp | No | 3 | 14 | 42
| 13 01 00 0015 | (f) Tinned Copper Fuse Wire No.14(for 63 Amp. Fuse) | Grams | 6 | 0.7 | 4.2
| 13 01 00 0015 | (g) Tinned Copper Fuse Wire No.14(for 32 Amp. Fuse) | Grams | 0 | 0.7 | 0
| 04 15 00 0003 | (h)Alu.lugs -Trans. LT 70 SQ.MM Cable | NO. | 6 | 8.9 | 53.4
| 04 15 00 0004 | (i)Alu.lugs -Trans. LT 35 SQ.MM Cable | NO. | 2 | 3.54 | 7.08
| 04 16 00 0006 | (j)Alu.lugs for kit-Kat 25 SQ.MM Cable | NO. | 6 | 3.2 | 19.2
| 04 16 00 0005 | (k)Alu.lugs for kit-Kat 16 SQ.MM Cable | NO. | 2 | 2.7 | 5.4
| 26 13 00 0002 | (I) Three hole patties | NO. | 6 | 30 | 180
| 26 01 00 0049 | (j) Side Clamp | NO. | 12 | 65 | 780
2496.78
14 |  | COST OF MATERIALS |  |  |  | 47396.96
15 |  | A |  |  |  | 47396.96
|  | ADD:3% CONTINGENCIES |  |  |  | 1421.9088
|  | ADD:2% STORAGE CHARGES |  |  |  | 947.9392
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 947.9392
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 7109.544
|  | Total ….A |  |  |  | 57824.2912
16 |  | LABOUR CHARGES FOR ERECTION OF T/C.INCL.
PAINTINGING OF STRUCTURE MATERIAL AND
PROVIDING LIGHTENING ARRESTOR,HG FUSES,
|  | DIST.BOX ETC. | NO. | 1 | 6899 | 6899
17 |  | ERECTION OF EARTHING COIL | NO. | 3 | 419 | 1257
PLATE TYPE WITH SALT &COAL
18 |  | ERECTION OF GUY SET COMPLETE | NO. | 4 | 364 | 1456
19 |  | CARTING OF POLE AT WORK SITE | NO. | 2 | 246 | 492
20 |  | CARTING OF LINE MATERIALS TO SITE |  |  | ---LS--- | 575
21 |  | CONCRETING OF GUY WITH MATERIAL(1:2:4) | CMT | 1.96 | 5900 | 11564
22 |  | INSTALLATION OF ENERGY METER,MM BOX ETC. |  |  | ---LS--- | 550
ON T/C
23 |  | LABOUR CHARGES… |  |  |  | 22793
24 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3418.95
25 |  | B |  |  |  | 26211.95
26 |  | Sub Total(A+B) |  |  |  | 84036.2412
|  | Total Estimate |  |  | Say Rs. | 84036.2412

## H26.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 26
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
RIVER CROSSING USING 10 MTR PSC POLES FOR 11KV
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 26 11 00 0003 | PSC POLE 10Mtr. (270KG) | NO. | 4 | 3505 | 14020
2 |  | TOP CROSS ARMS FOR TERMINATING | NO. | 4 | 834 | 3336
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750 mm for top cross arm for terminating line | No | 4 | 834 | 3336
3 |  | BRACING FOR DOUBLE POLENSTRUCTURE | SET | 2 | 3336 | 6672
( 4 angles perset)
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV | No. | 4 | 834 | 3336
4 |  | 11 KV STRAIN INSULATOR H/W WITH | SET | 12 | 292 | 3504
PREFORMED FITTING
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 1 | 128 | 128
292
5 |  | ANTI-CLIMBING DEVICES. | NO. | 4 | 120 | 480
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 4 | 120 | 480
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 4 | 60 | 240
7 |  | EARTHING OF D.P. STRUCTURE | NO. | 4 | 438 | 1752
Material required for 1 No. Pipe Type earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 1 Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (e) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (f) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | GUY SET WITH PREFORMED FITTING | NO. | 8 | 1057 | 8456
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
9 |  | SUNDRY MATERIAL SUCH AS BOLT & |  |  |  | 1498.6
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 70 | 336
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 4.98 | 70 | 348.6
| 26 01 00 0027/0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 19 05 00 0006 | (d) HT Tape for binding | Mtr | 10 | 13 | 130
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.2 | 120 | 24
1498.6
10 |  | COST OF MATERIALS |  |  |  | 39958.6
11 |  | A |  |  |  | 39958.6
|  | ADD:3% CONTINGENCIES |  |  |  | 1198.758
|  | ADD:2% STORAGE CHARGES |  |  |  | 799.172
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 799.172
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 5993.79
|  | Total ….A |  |  |  | 48749.492
12 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON PSC POLE . | NO. | 2 | 4030 | 8060
13 |  | INSTALLATION OF EARTHING COIL | NO. | 4 | 419 | 1676
PLATE TYPE WITH SALT &COAL
14 |  | PROVIDING GUY SET COMP.WITH | NO. | 8 | 364 | 2912
ALL ACCESSORES &FITTING
15 |  | CARTING OF PSC POLE AT DEST. | NO. | 4 | 400 | 1600
16 |  | CARTING OF MATERIAL AT WORK SITE |  |  | ----LS---- | 575
17 |  | CONCRETING OF GUY & RSJ POLES WITH MATERIAL(1:2:4) | CMT | 1.2 | 5900 | 7080
18 |  | LABOUR CHARGES.. |  |  |  | 21903
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 3285.45
20 |  | B |  |  |  | 25188.45
21 |  | Sub Total(A+B) |  |  |  | 73937.942
|  | Total Estimate |  |  | Say Rs. | 73937.942

## H27.
UTTAR GUJARAT VIJ COMPANY LIMITED |  |  |  |  | COST DATA
ITEM 27
COST DATA FOR HT POWER SUPPLY FOR FY 2019-20
RIVER CROSSING USING 11 MTR RSJ POLES FOR 11KV
SR | ITEM CODE NO. | PARTICULARS | UNIT | QTY | UNIT RATE | AMOUNT
NO |  |  |  |  | (RS). | (RS.)
1 | 3604000036 | RSJ POLE 116*100*11 Meter | NO. | 4 | 12986 | 51944
2 |  | TOP CROSS ARMS FOR TERMINATING | NO. | 4 | 834 | 3336
| 36 11 00 0016 | M.S.Angle 65x65x6mm - 2750 mm for top cross arm for terminating line | No | 4 | 834 | 3336
3 |  | BRACING FOR DOUBLE POLENSTRUCTURE | SET | 2 | 3336 | 6672
( 4 angles perset)
| 36 11 00 0028 | M.S. Angle Fabri. 65x65x6mm - 2750mm for cross bracing - 11KV | No. | 4 | 834 | 3336
4 |  | 11 KV STRAIN INSULATOR H/W WITH | SET | 12 | 292 | 3504
PREFORMED FITTING
| 20 06 00 0001 | (a) 11 KV Disc. Insulator | NO. | 1 | 164 | 164
| 20 10 00 0007 | (b) 11 KV Disc. Hardware | SET | 1 | 128 | 128
292
5 |  | ANTI-CLIMBING DEVICES. | NO. | 4 | 120 | 480
| 01 03 00 0070 | Barbed wire - 1.591 Kg for 1 No. anticlimning device | NO. | 4 | 120 | 480
30.192
6 | 26 99 00 0006 | CAUTION & DANGER BOARD. | NO. | 4 | 60 | 240
7 |  | EARTHING OF D.P. STRUCTURE | NO. | 4 | 438 | 1752
Material required for 1 No. Pipe Type earthing
| 01 03 00 0002 | (a ) GI Wire No. 8 - 1 Kg | KG | 1 | 73 | 73
| 28 01 00 0015 | (b) Rigid PVC Pipe -20mm dia ( 1.5 Mtr) - 1No | NO. | 1 | 43 | 43
| 09 01 00 0007 | (e) C.I. Earthing plate - 300x300x9mm - 1 No | NO. | 1 | 313 | 313
| 09 01 00 0028 | (f) Earthing Bolt -1 No. | NO. | 1 | 9 | 9
438
8 |  | GUY SET WITH PREFORMED FITTING | NO. | 8 | 1057 | 8456
Material required for1 No. Guy set
| 26 14 00 0002 | (a) Ancher rod - 1 No. | NO. | 1 | 258 | 258
| 26 14 00 0009 | (b) Turn buckle - 1 No. | NO. | 1 | 145 | 145
| 26 14 00 0012 | (c) Eye Bolt - 1No. | NO. | 1 | 74 | 74
| 01 03 00 0012 | (d) Stay wire- 7/10 5 Kg. | KG | 5 | 73 | 365
| 20 03 00 0001 | (e) HT Guy Insulator - 1 No. | NO. | 1 | 30 | 30
| 26 01 00 0069 | (f) Guy Clamp - 1 Set. | SET | 1 | 180 | 180
| 2614000017 | (g) Thimble for HT/LT Line | NO | 1 | 5 | 5
1057
9 |  | SUNDRY MATERIAL SUCH AS BOLT & |  |  |  | 1396.6
NUTS/PG CLAMPS/BINDING TAPE &
BINDING WIRE ETC. WITH PREFORMD
FITTING.
| 15 01 00 0024 | (a) M.S. Bolts & Nuts 65x16mm | KG | 4.8 | 70 | 336
| 15 01 00 0031 | (b) M.S. Bolts & Nuts 180x16mm | KG | 4.98 | 70 | 348.6
| 26 01 00 0027/0028 | (c) P.G. Clamp for Weasel or Rabbit | No | 6 | 110 | 660
| 19 05 00 0006 | (d) HT Tape for binding | Mtr | 10 | 2 | 20
| 01 01 00 0003 | (e) Alu. Binding wire | KG | 0.2 | 160 | 32
1396.6
10 |  | COST OF MATERIALS |  |  |  | 77780.6
11 |  | A |  |  |  | 77780.6
|  | ADD:3% CONTINGENCIES |  |  |  | 2333.418
|  | ADD:2% STORAGE CHARGES |  |  |  | 1555.612
|  | ADD:2% TRANSPORTATION & MISC. |  |  |  | 1555.612
|  | ADD:15% SUPERVISION CHARGES ON COST OF MATERIALS |  |  |  | 11667.09
|  | Total ….A |  |  |  | 94892.332
12 |  | LABOUR CHARGES FOR ERECTION OF D.P.
|  | STRUCTURE ON RSJ POLE . | NO. | 2 | 2485 | 4970
13 |  | INSTALLATION OF EARTHING COIL | NO. | 4 | 419 | 1676
PLATE TYPE WITH SALT &COAL
14 |  | PROVIDING GUY SET COMP.WITH | NO. | 8 | 364 | 2912
ALL ACCESSORES &FITTING
15 |  | CARTING OF RSJ POLE AT DEST. | NO. | 4 | 246 | 984
16 |  | CARTING OF MATERIAL AT WORK SITE |  |  | ----LS---- | 575
17 |  | CONCRETING OF GUY & RSJ POLES WITH MATERIAL(1:2:4) | CMT | 3.92 | 5900 | 23128
18 |  | LABOUR CHARGES.. |  |  |  | 34245
19 |  | ADD:15% SUPERVISION CHARGE ON LABOUR CHARGES |  |  |  | 5136.75
20 |  | B |  |  |  | 39381.75
21 |  | Sub Total(A+B) |  |  |  | 134274.082
|  | Total Estimate |  |  | Say Rs. | 134274.082